## Revision
INDEX | DESCRIPTION | DATE | AUTHOR
1 | Prima emissione | 2012-09-27 | M.DiCecca
2 | aggiornate schede unit list e standard list e revisionate tutte le altre | 2013-02-07 | M.DiCecca
3 | aggiornato e prima versione gestita nel programma aurora_ analyzer | 2013-02-07 | M.DiCecca
4 | ……. | 2013-03-05 | M.DiCecca
5 | aggiunto foglio FlickerValue | 2013-03-05 | M.DiCecca
6 | aggiornati nomi dei certificati | 2013-03-06 | M.DiCecca
7 | aggiornati i nomi dei certificati | 2013-03-11 | M.DiCecca
8 | aggiunti modelli PVI-250(500) | 2013-03-11 | M.DiCecca
9 | aggiunti valori scalature pvi-6000 e pvi-4.2 | 2013-03-19 | M.DiCecca
10 | …….. | 2013-03-28 | M.DiCecca
11 | aggiunto trio-7.5 | 2013-03-28 | M.DiCecca
12 | aggiunti modelli centralizzati in aurora unit list | 2013-04-09 | M.DiCecca
13 | aggiunti modelli ultra | 2013-05-03 | M.DiCecca
14 | aggiunti standard japan 50 e 60 e EN50438 in Aurora_standardList | 2013-05-06 | M.DiCecca
15 | aggiornati nomi modelli ultra | 2013-05-06 | M.DiCecca
16 | aggiunto modello PVI-MODULE-390kVA | 2013-06-12 | M.DiCecca
17 | aggiornati id label scheda aurora_list allineati ai nomi nel variable matrix | 2013-06-19 | M.DiCecca
18 | aggiornato nome certificato francia | 2013-06-19 | M.DiCecca
19 | aggiunto standard france vrf residential | 2013-06-21 | M.DiCecca
20 | Corrette famiglie TRIO 8.5 | 2013-07-01 | L.Bellosi
21 | Inserita sche LossofMain e flicher TRIO-8.5 | 2013-07-04 | L.Bellosi
22 | Corretti Modelli PVI-280.0-TL e PVI-560.0-TL | 2013-07-04 | G.Testi
23 | Modificato id CINA | 2013-07-04 | M.DiCecca
24 | Inserito modello PVI-13.8(11.0)-TL-OUTD | 2013-07-05 | M.DiCecca
25 | adattato il file all'importazione da aurora dvt ver.72 | 2013-07-09 | M.DiCecca
26 | aggiunta scheda ShortCircuit | 2013-07-09 | M.DiCecca
27 | aggiornamenti vari aurora protocol | 2013-09-17 | M.DiCecca
28 | aggiornato aurora protocol e corretti nomi degli standard in Aurora_standardList | 2013-09-17 | M.DiCecca
29 | Allineato documento a "DisplayLabels_NameStandards_rev7.xlsx". Da oggi il presente documento verrà usato al posto del "DisplayLabels_NameStandards_rev7.xlsx" per portarne avanti uno soltanto. | 2013-09-17 | T. Bucci
30 | aggiornata lista Global State | 2013-09-18 | M.DiCecca
31 | aggiornata scheda cmd_59 con etichette per il programma DVT | 2013-09-19 | M.DiCecca
32 | aggiunti modelli UNO-8.5-7.5 e Reac-4.6-3.6 | 2013-11-14 | M.DiCecca
33 | aggiunti standard VDE0126-3W | 2013-12-18 | M.DiCecca
34 | aggiornati foglio FlickerValue per UNO 2.5(2.0) | 2014-01-22 | S.Giovannetti
35 | aggiornati tutta la scheda aurora grid standards list | 2014-02-11 | M.DiCecca
36 | Aggiunta scheda ModBus_React | 2014-03-18 | M.DiCecca
37 | Aggiunte sche ModBus aggiornati format delle schede e riordinate aggiunti campi code in IsWind e IsTransformer, aggiunta scheda ModBus_InvType | 2014-03-24 | M.DiCecca
38 | Aggiunte schede degli stati della batteria del react e caric RLC ancora da definire | 2014-03-24 | M.DiCecca
38 | modificata lista cmd 59 | 2014-05-19 | M.DiCecca
39 |  | 2014-05-19 | M.DiCecca
40 | Aggiornata scheda Modbus_carcioRLC | 2014-05-28 | M.DiCecca
41 | Aggiornata scheda gaurora standard list aggiornati cina a cina LV e cina cqc a cina HV modificato id india da q a 2 | 2014-06-16 | M.DiCecca
42 | Aggiornati label scheda ModBus RLC 30KVA | 2014-06-23 | M.DiCecca
43 | Revisionati nomi degli standard JAPAN in JP nel foglio "Specchietto" | 2014-06-23 | D.Palumbo
44 | Revisionati fogli carico RLC3ph | 2014-07-07 | M.DiCecca
45 | Attivati registri FC e IC Battery | 2014-07-07 | M.DiCecca
46 | Allineata alla Mappa 0.13 del ModBus del BMS REACT | 2014-07-09 | M.DiCecca
47 | Aggiornate pagine protocollo aurora V5.1.1 | 2014-07-15 | M.DiCecca
48 | Eliminate schede che non appartengono all'aurora protocol | 2014-07-15 | M.DiCecca
49 | Inserito comando per gestione React | 2014-12-16 | M.DiCecca
50 | Modificati nomi dei label delle misure dell'aurora | 2015-01-12 | M.DiCecca
51 | Aggiunte misure sul comando 59 versione protocollo 5.1.5 | 2015-01-29 | M.DiCecca
52 | Aggiornati registri comando 78 | 2015-03-02 | M.DiCecca
53 | Aggiunte Energie comando 78, Self-Consumption e Self-Sufficiency comando 59 | 2015-03-02 | M.DiCecca
54 | …… | 2015-07-02 | M.DiCecca
55 | corretta label Urms1 e irms1 a mean | 2015-07-02 | M.DiCecca
56 | Aggiornati gli Alarm_State | 21/07/2016 | M.DiCecca
57 | Aggiornato lo sheet "cmd_59" con la lista delle grandezze reserved per il modello TRIO-50.0-TL-OUTD. | 2016-09-29 | G.Testi
58 | Nello sheet "cmd_59" aggiunte le grandezze AUR_IDC3, AUR_PDC3 e AUR_UDC3 per TRIO-TM-50.0(60.0)-TL-OUTD. | 2017-03-21 | G.Testi
59 | aggiunte colonne cmd_59 per supportare cmd 146 | 2017-04-26 | M.DiCecca
60 | Aggiunte letture DcInjection e Leakage su cmd 146 | 2017-04-26 | D.Palumbo
61 | Nello sheet "cmd_59" aggiunte le grandezze AUR_UDC4, AUR_IDC4, AUR_PDC4, AUR_UDC5, AUR_IDC5, AUR_PDC5, AUR_UDC6, AUR_IDC6, AUR_PDC6 per PVS-120.0-TL. | 2017-07-04 | G.Monti
62 | Nello sheet "cmd_59" in colonna "label_dvt", le misure relative alla componente DC Injection relative alle coppie [id=60,cmd=146] [id=61,cmd=146], [id=62,cmd=146] sono state rietichettate rispettivamente come AUR_Idc1, AUR_Idc2 e AUR_Idc3 | 2017-07-24 | F. Pelliccia
63 | Aggiunte misure cmd_59 | 2017-08-23 | G.Lombardi
64 | Aggiunto codice allarme 161 "E093 - Generic HW Latch" | 2017-08-29 | F. Pelliccia
65 | Aggiunto misura cmd_59-254 "Voltage after LP filter in input of Volt-Watt Function" | 2017-09-28 | M.Cavallina
66 | Nello sheet "cmd_59" modificata id su AUR_UDC6 per PVS-120.0-TL e PVS-100-TL. | 2017-11-13 | G.Monti
67 | Aggiunto misura cmd_146-384 "Freq.LP filter for Freq-Watt". | 2017-11-20 | D.Palumbo
68 | Modificato nome inverter da TRIO-100.0 a PVS-120(100)-TL su sheet 'cmd_59 label' su id 192. 193, 194, 195, 196, 197, 198, 199, 204. | 2017-11-24 | G.Monti
65 | Aggiunto misura cmd_59-255 "Voltage after LP filter in input of Volt-Var Function". Revisionati nomi filtri LP di Volt-Watt, Freq-Watt e Volt-Var per compatibilità con programma ATP. | 2017-12-20 | D.Palumbo

## Alarm_State
id | desc | code
0 | No Alarm | ---
1 | Sun Low | W001
2 | Input OC | E001
3 | Input UV | W002
4 | Input OV | E002
5 | Sun Low | W001
6 | No Parameters | E003
7 | Bulk OV | E004
8 | Comm.Error | E005
9 | Output OC | E006
10 | IGBT Sat | E007
11 | Bulk UV | W011
12 | Internal error | E009
13 | Grid fault | W003
14 | Bulk UV | E010
15 | Ramp Fault | E011
16 | Dc/Dc Fail | E012
17 | Wrong input mode | E013
18 | Ground Fault | ---
19 | Over Temp. | E014
20 | Bulk Cap Fail | E015
21 | Inverter Fail | E016
22 | Start Timeout | E017
23 | Leak fault | E018
24 | AC feed forward | E049
25 | Ileak sens.fail | E019
26 | DcDc Fail | E012
27 | Self Test Error 1 | E020
28 | Self Test Error 2 | E021
29 | Self Test Error 3 | E019
30 | Self Test Error 4 | E022
31 | DC injection | E023
32 | Grid OV | W004
33 | Grid UV | W005
34 | Grid OF | W006
35 | Grid UF | W007
36 | Z grid Hi | W008
37 | Internal error | E024
38 | Riso Low | E025
39 | Vref Error | E026
40 | Error Meas V | E027
41 | Error Meas F | E028
42 | Mid bulk OV | E029
43 | Error Meas Ileak | E030
44 | Error Read V | E031
45 | Error Read I | E032
46 | No power curve | W009
47 | Fan fault | W010
48 | Undertemperature | E033
49 | IGBT not ready | E034
50 | Remote Off | E035
51 | Vout Avg error | E036
52 | Battery low | W012
53 | Clock fault | W013
54 | Riso low | E037
55 | Zero Power | W014
56 | Fan failed | E038
57 | DC switch opened | E039
58 | Mod.Cont opened | E040
59 | AC switch Opened | E041
60 | Bulk UV | E042
61 | Autoexclusion | E043
62 | Island. Detected | W015
63 | DC SPD tripped | W016
64 | Jbox fault | W017
65 | DC door opened | E044
66 | AC door opened | E045
67 | AntiIsland.Fault | E047
68 | DC fuse fault | W020
69 | Chiller Gen Fail | E048
70 | DC SPD tripped | W018
71 | AC SPD tripped | W019
72 | Str. test failed | E046
73 | P-reductionStart | W021
74 | P-reductionEnd | W025
75 | Q-modeChange | W022
76 | Date/time mod. | W023
77 | Energy data rst | W024
78 | Riso Test Fail | E078
79 | AFDD activated | E050
80 | Safety mem.Fault | E051
81 | Mod. Door opened | E052
82 | AFDD fault | E053
83 | AFDD comm. Fault | E054
84 | AFDD user reset | W026
85 | AFDD wrong conf. | E055
86 | OTH SC | E056
87 | Vbulk reading | E057
88 | Pin vs Pout check error | E058
89 | Latch-Manual rst | W027
90 | Periodic GridOff | W048
91 | Riso Low a. (AC side test) | E077
92 | OVGR (fail at utility side) | E060
93 | RPR (fail at plant side) | E061
94 | No AC production timeout | W029
95 | Grid conn. fault | W046
96 | Latch-Manual ent | E075
97 | IGBT power driver fail | E063
98 | HW OC | E064
99 | GPIO fault | E076
100 | Energy Meter ERROR | W030
101 | Stop Button | E065
102 | T Sensor Warning | W050
103 | T Sensor Fault | E080
104 | System Stop | E082
105 | BMS fault | W031
106 | Internal error | E074
107 | Sys disconnected | W045
108 | SOH Low | W053
109 | SOH Low ( Fault ) | W054
110 | Batt. 1 - W | W036
111 | Batt. 1 - F1 | W037
112 | Batt. 1 - F2 | E086
113 | Batt. 2 - W | W039
114 | Batt. 2 - F1 | W040
115 | Batt. 2 - F2 | E087
116 | Batt. 3 - W | W042
117 | Batt. 3 - F1 | W043
118 | Batt. 3 - F2 | E088
119 | Battery Low ( 0% ) | W055
120 | Polarity Inversion Fault | E083
121 | Power Engage | W056
122 | COMMISSIONING - SOH test - Warning | W060
123 | COMMISSIONING - SOH test - Fault | W061
124 | BMS Shutdown Failed | W062
125 | Force Grid Disconnection for SA Request | W063
126 | Grounding Error | E090
127 | Battery Firmware Update Failed | W064
130 | Charger-Bulk | E066
131 | Charger - OV | E067
132 | Charger - OC | E068
133 | Charger-SlowRamp | E069
134 | Charger-preChar. | E070
135 | Microinverter - Fgrid Not Ok | W035
136 | Microinverter - Country Standard Mismatch | E071
137 | Microinverter - Country Standard Not Compatible | E072
138 | Microinverter - Country Standard Not Valid | E073
139 | Microinverter - Inverter Comm Warning | W501
140 | Microinverter - Zero Production Warning | W502
141 | Microinverter - Firmware Upgrade in progress | W603
142 | Inverter Comm Fault | E501
143 | Zero production alarm | E502
144 | HW Module Swap | W065
145 | Brake Board Test Fault | E091
146 | Brake Board Test Warning | W066
147 | PSU Power Good Alarm | E092
148 | Loss of Control | E085
149 | Low Auxiliary Voltage | W057
150 | UpdateIncomplete | W047
151 | Global-Settings Event | W049
152 | Wrong Sequence | E079
153 | Internal error | E081
154 | Exit From SA | W051
155 | RISO Check Bypassed | W052
156 | BackFeed OC | E084
157 | System Frozen | W058
158 | Output Power Overload | W059
159 | Wrong Wiring | E089
160 | ID Data Was Set | W067
161 | Generic HW Latch | E093

## Global_State
id | desc
0 | Sending Parameters
1 | Wait Sun/Grid
2 | Checking Grid
3 | Measuring Riso
4 | DcDc Start
5 | Inverter Start
6 | Run
7 | Recovery
8 | Pause
9 | Ground Fault
10 | OTH Fault
11 | Address Setting
12 | Self Test
13 | Self Test Fail
14 | Sensor Test + Meas.Riso
15 | Leak Fault
16 | Waiting for manual reset
17 | Internal Error E026
18 | Internal Error E027
19 | Internal Error E028
20 | Internal Error E029
21 | Internal Error E030
22 | Sending Wind Table
23 | Failed Sending table
24 | UTH Fault
25 | Remote OFF
26 | Interlock Fail
27 | Executing Autotest
28 | Waiting Sun
29 | Temperature Fault
30 | Fan Staucked
31 | Int. Com. Fault
32 | Slave Insertion
33 | DC Switch Open
34 | TRAS Switch Open
35 | MASTER Exclusion
36 | Auto Exclusion
98 | Erasing Internal Eeprom
99 | Erasing External Eeprom
100 | Counting Eeprom
101 | Freeze
110 | Forbidden partner board was found
111 | DC string self-test fault
112 | Service Mode
113 | “Safety” memory area error
114 | Too many leak fault events for the day
115 | Arc fault
116 | Power Off
117 | Communication loss with Communication Board
118 | Arc Detector configuration
119 | Arc detector self test
120 | Wrong model code
121 | Hardware config refused
122 | V bulk fault
123 | Pin vs Pout fault
150 | DSP communication error
200 | Dsp Programming

## Inverter_State
id | desc
0 | Stand By
1 | Checking Grid
2 | Run
3 | Bulk OV
4 | Out OC
5 | IGBT Sat
6 | Bulk UV
7 | Degauss Error
8 | No Parameters
9 | Bulk Low
10 | Grid OV
11 | Comunication Error
12 | Degaussing
13 | Starting
14 | Bulk Cap Fail
15 | Leak Fail
16 | DcDc Fail
17 | Ileak Sensor Fail
18 | SelfTest: relay inverter
19 | SelfTest: wait for sensor test
20 | SelfTest: test relay DcDc + sensor
21 | SelfTest: relay inverter fail
22 | SelfTest timeout fail
23 | SelfTest: relay DcDc fail
24 | Self Test 1
25 | Waiting self test start
26 | Dc Injection
27 | Self Test 2
28 | Self Test 3
29 | Self Test 4
30 | Internal Error
31 | Internal Error
40 | Forbidden State
41 | Input UC
42 | Zero Power
43 | Grid Not Present
44 | Waiting Start
45 | MPPT
46 | Grid Fail
47 | Input OC
255 | Inverter Dsp not programmed

## DcDc_State
id | desc
0 | DcDc OFF
1 | Ramp Start
2 | MPPT
3 | Not Used
4 | Input OC
5 | Input UV
6 | Input OV
7 | Input Low
8 | No Parameters
9 | Bulk OV
10 | Comunication Error
11 | Ramp Fail
12 | Internal Error
13 | Input mode Error
14 | Ground Fault
15 | Inverter Fail
16 | DcDc IGBT Sat
17 | DcDc ILEAK Fail
18 | DcDc Grid Fail
19 | DcDc Comm. Error
255 | DcDc Dsp not programmed

## IsTransformer
id | desc | code
N | Transformerless version | 78
T | Transformer version | 84
t | Transformer HF version | 116
X | Dummy transformer type | 120

## IsWind
id | desc | code
N | Photovoltaic version | 80
W | Eolic version | 87
x | Dummy inverter type | 120
n | Energy Storage System | 110

## cmd_59
id | cmd | label | inverter | label_dvt | Device | TypeMeas
65 | 59 | Cos-phi setpoint target value for reactive power regulation | All, excluding PVI-2000. PVI-2000-OUTD, PVI-3600, PVI-3600-OUTD | AUR_COS_SET | 0 | 0
104 | 59 | Delta P after PV scan [W] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_DELTA_P | 0 | 0
80 | 59 | Fan 3 speed [rpm] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_F_3 | 0 | 0
4 | 59 | Frequency (Hz) | All For three-phases systems is the mean | AUR_FU | 0 | 0
29 | 59 | Grid Frequency (Dc/Dc) (Hz) | Aurora grid-tied only | AUR_FU_DCDC | 0 | 0
42 | 59 | Frequency phase r (Hz) | Central models, PVI OUTD 3-phase models | AUR_FU1 | 0 | 0
43 | 59 | Frequency phase s (Hz) | Central models, PVI OUTD 3-phase models | AUR_FU2 | 0 | 0
44 | 59 | Frequency phase t (Hz) | Central models, PVI OUTD 3-phase models | AUR_FU3 | 0 | 0
79 | 59 | Average GND voltage [V] | TRIO-27.6-TL and TRIO-27.6-TL only | AUR_GND_AVG_V | 0 | 0
83 | 59 | Ground voltage [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_GND_V | 0 | 0
109 | 59 | Grid current offset for DC injection compensation phase R [mA] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_Idc_C_R | 0 | 0
110 | 59 | Grid current offset for DC injection compensation phase S [mA] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_Idc_C_S | 0 | 0
111 | 59 | Grid current offset for DC injection compensation phase T [mA] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_Idc_C_T | 0 | 0
25 | 59 | Input 1 Current (A) | All Input Current for single channel module | AUR_IDC1 | 0 | 0
27 | 59 | Input 2 Current (A) | Aurora grid-tied only Measurement not significant for single channel modules. | AUR_IDC2 | 0 | 0
6 | 59 | Ileak (Dc/Dc) | Aurora grid-tied only | AUR_ILEAK_DcDc | 0 | 0
7 | 59 | Ileak (Inverter) | Aurora grid-tied only | AUR_ILEAK_Inv | 0 | 0
2 | 59 | Grid Current (A) | All For three-phases systems is the mean | AUR_IRMS1 | 0 | 0
39 | 59 | Grid Current phase r (A) | Central models, PVI OUTD 3-phase models | AUR_IRMS1 | 0 | 0
40 | 59 | Grid Current phase s (A) | Central models, PVI OUTD 3-phase models | AUR_IRMS2 | 0 | 0
41 | 59 | Grid Current phase t (A) | Central models, PVI OUTD 3-phase models | AUR_IRMS3 | 0 | 0
94 | 59 | Isolation quality factor (Iso QF) | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_ISO_QF | 0 | 0
32 | 59 | Average Grid Voltage r (VgridAvg) (V) | Aurora grid-tied only | AUR_MAXAVG_R | 0 | 0
69 | 59 | Average Grid Voltage s (VgridAvg) (V) | Aurora grid-tied only | AUR_MAXAVG_S | 0 | 0
70 | 59 | Average Grid Voltage t (VgridAvg) (V) | Aurora grid-tied only | AUR_MAXAVG_T | 0 | 0
77 | 59 | Actual power versus nominal power ratio | All, excluding PVI-2000. PVI-2000-OUTD, PVI-3600, PVI-3600-OUTD | AUR_P_ACTUAL | 0 | 0
64 | 59 | Actual applied power limit [W] | All, excluding PVI-2000. PVI-2000-OUTD, PVI-3600, PVI-3600-OUTD | AUR_P_LIM | 0 | 0
78 | 59 | Nominal power [W] | All, excluding PVI-2000. PVI-2000-OUTD, PVI-3600, PVI-3600-OUTD | AUR_P_NOM | 0 | 0
34 | 59 | Power Peak (W) | All | AUR_P_Peak | 0 | 0
35 | 59 | Power Peak Today (W) | All | AUR_P_Peak_Today | 0 | 0
8 | 59 | Pin1 | All | AUR_PDC1 | 0 | 0
9 | 59 | Pin2 | Aurora grid-tied only Measurement not significant for single channel modules. | AUR_PDC2 | 0 | 0
3 | 59 | Grid Power (W) | All For three-phases systems is the mean | AUR_PoutTot | 0 | 0
112 | 59 | Q-set point applied | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_Q_SET | 0 | 0
183 | 59 | Input 1 Voltage - Redundant [V] | Aurora grid-tied only | AUR_REDUNDANT_UDC1 | 0 | 0
184 | 59 | Input 2 Voltage - Redundant [V] | Aurora grid-tied only | AUR_REDUNDANT_UDC2 | 0 | 0
30 | 59 | Isolation Resistance (Riso) (MT) | All | AUR_RISO | 0 | 0
107 | 59 | Ground voltage read by DC/AC module with test relay closed [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCAC_CLOSE | 0 | 0
81 | 59 | R-ISO measured by DC/AC module M1 [MOhm] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCAC_M1 | 0 | 0
82 | 59 | R-ISO measured by DC/AC module M2 [MOhm] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCAC_M2 | 0 | 0
105 | 59 | Ground voltage read by DC/AC module with test relay open [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCAC_OPEN | 0 | 0
108 | 59 | Ground voltage read by DC/DC module with test relay closed [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCDC_CLOSE | 0 | 0
106 | 59 | Ground voltage read by DC/DC module with test relay open [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_RISO_DCDC_OPEN | 0 | 0
22 | 59 | Booster Temperature (°C) | Aurora grid-tied only | AUR_T_DCDC | 0 | 0
22 | 59 | Tbst_A (°C) | TRIO-50.0 only | TRIO50_Tbst_A | 0 | 0
21 | 59 | Inverter Temperature (°C) | Aurora grid-tied only | AUR_T_INV | 0 | 0
21 | 59 | Tinv_R_top | TRIO-50.0 only | TRIO50_Tinv_R_top | 0 | 0
23 | 59 | Input 1 Voltage (V) | Input Voltage for single channel module | AUR_UDC1 | 0 | 0
26 | 59 | Input 2 Voltage (V) | Aurora grid-tied only Measurement not significant for single channel modules. | AUR_UDC2 | 0 | 0
36 | 59 | Grid Voltage neutral (V) | Aurora grid-tied only | AUR_URMS_NEUTRAL | 0 | 0
1 | 59 | Grid Voltage (V) | All For three-phases systems is the mean | AUR_URMS1 | 0 | 0
61 | 59 | Grid Voltage phase r (V) | Central models, PVI OUTD 3-phase models | AUR_URMS1 | 0 | 0
28 | 59 | Grid Voltage (Dc/Dc) (V) | Aurora grid-tied only | AUR_URMS1_DCDC | 0 | 0
93 | 59 | Grid peak voltage [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_URMS1_PEAK | 0 | 0
85 | 59 | Grid voltage R-S [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_URMS12 | 0 | 0
62 | 59 | Grid Voltage phase s (V) | Central models, PVI OUTD 3-phase models | AUR_URMS2 | 0 | 0
86 | 59 | Grid voltage S-T [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_URMS23 | 0 | 0
63 | 59 | Grid Voltage phase t (V) | Central models, PVI OUTD 3-phase models | AUR_URMS3 | 0 | 0
87 | 59 | Grid voltage T-R [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_URMS31 | 0 | 0
185 | 59 | V neutral DCDC | Aurora monophase TL - Rule 21 | AUR_V_NEUTRAL_DCDC | 0 | 0
186 | 59 | V phase-neutral DCDC | Aurora monophase TL - Rule 21 | AUR_V_PN_DCDC | 0 | 0
5 | 59 | Vbulk (V) | All For Inverter with more than one bulk is the sum | AUR_VBULK | 0 | 0
90 | 59 | Bulk voltage set-point for DC/AC module [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_VBULK_DCAC_SET | 0 | 0
31 | 59 | Vbulk (Dc/Dc) (V) | Aurora grid-tied only | AUR_VBULK_DCDC | 0 | 0
91 | 59 | Bulk voltage set-point for DC/DC module [V] | TRIO-27.6-TL, TRIO-5.8(7.5)(8.5)-TL-OUTD-400, PVI-12.5(10.0,8.0,6.0)-TLOUTD only | AUR_VBULK_DCDC_SET | 0 | 0
45 | 59 | Vbulk + (V) | Central models, PVI OUTD 3-phase models | AUR_VBULK_P | 0 | 0
33 | 59 | VbulkMid (V) | Aurora grid-tied only | AUR_VBULKMID | 0 | 0
59 | 59 | Bulk Loop Reference (V) CENTRAL | Central only | CENTRAL_BULK_REF | 0 | 0
53 | 59 | Fan 1 Speed (rpm) CENTRAL | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_F_1 | 0 | 0
53 | 59 | Fan_Pack_1 | TRIO-50.0 only | TRIO50_Fan_Pack_1 | 0 | 0
95 | 59 | Fan 6 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_1 | 0 | 0
95 | 59 | Fan_Module | TRIO-50.0 only | TRIO50_Fan_Module | 0 | 0
54 | 59 | Fan 2 Speed (rpm) CENTRAL | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_F_2 | 0 | 0
54 | 59 | Fan_Pack_2 | TRIO-50.0 only | TRIO50_Fan_Pack_2 | 0 | 0
96 | 59 | Fan 7 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_2 | 0 | 0
55 | 59 | Fan 3 Speed (rpm) CENTRAL | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_F_3 | 0 | 0
55 | 59 | Fan_Pack_3 | TRIO-50.0 only | TRIO50_Fan_Pack_3 | 0 | 0
97 | 59 | Fan 8 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_3 | 0 | 0
56 | 59 | Fan 4 Speed (rpm) CENTRAL | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_F_4 | 0 | 0
56 | 59 | Fan_Pack_4 | TRIO-50.0 only | TRIO50_Fan_Pack_4 | 0 | 0
98 | 59 | Fan 9 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_4 | 0 | 0
57 | 59 | Fan 5 Speed (rpm) CENTRAL | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_F_5 | 0 | 0
57 | 59 | Fan_AC_box | TRIO-50.0 only | TRIO50_Fan_AC_box | 0 | 0
99 | 59 | Fan 10 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_5 | 0 | 0
100 | 59 | Fan 11 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_6 | 0 | 0
101 | 59 | Fan 12 Speed (rpm) CENTRAL250 | Central only Supported by PVI-CENTRAL-250 only | CENTRAL_F_7 | 0 | 0
58 | 59 | Power Saturation limit (Der.) (W) | Central only Not supported by PVI-CENTRAL-250 | CENTRAL_P_SAT | 0 | 0
102 | 59 | Patt Total | Central only | CENTRAL_PATT_TOT | 0 | 0
48 | 59 | Alim. Temperature (°C) CENTRAL | Central only | CENTRAL_T_ALI | 0 | 0
49 | 59 | Heat Sink Temperature (°C) CENTRAL | Central only | CENTRAL_T_HEAT | 0 | 0
47 | 59 | Supervisor Temperature (°C) CENTRAL | Central only | CENTRAL_T_MICRO | 0 | 0
50 | 59 | Temperature 1 (°C) CENTRAL CENTRAL | Central only | CENTRAL_T_T1 | 0 | 0
50 | 59 | T_DC_box_1 | TRIO-50.0 only | TRIO50_T_DC_box_1 | 0 | 0
51 | 59 | Temperature 2 (°C) CENTRAL | Central only | CENTRAL_T_T2 | 0 | 0
51 | 59 | T_DC_box_2 | TRIO-50.0 only | TRIO50_T_DC_box_2 | 0 | 0
52 | 59 | Temperature 3 (°C) CENTRAL | Central only | CENTRAL_T_T3 | 0 | 0
52 | 59 | Fan_DC_box | TRIO-50.0 only | TRIO50_Fan_DC_box | 0 | 0
38 | 59 | Grid Voltage neutral-phase (V) CENTRAL | Central only | CENTRAL_URMS1 | 0 | 0
46 | 59 | Vbulk – (V) CENTRAL | Central only | CENTRAL_VBULK_N | 0 | 0
60 | 59 | Vpanel micro (V) CENTRAL | Central only | CENTRAL_VPANEL | 0 | 0
155 | 59 | Fan_Duty_Inverter | TRIO-50.0 only | TRIO50_Fan_Duty_Inverter | 0 | 0
156 | 59 | Fan_Duty_Booster | TRIO-50.0 only | TRIO50_Fan_Duty_Booster | 0 | 0
157 | 59 | AC_P_Dissipated | TRIO-50.0 only | TRIO50_AC_P_Dissipated | 0 | 0
159 | 59 | GND_Kit_I_Rms | TRIO-50.0 only | TRIO50_GND_Kit_I_Rms | 0 | 0
176 | 59 | RTC_Battery_V | TRIO-50.0 only | TRIO50_RTC_Battery_V | 0 | 0
131 | 59 | Bulk Max ( Calculated ) | New architecture ABB Inverter | NEW_BULK_MAX | 0 | 0
130 | 59 | Bulk Min ( Calculated ) | New architecture ABB Inverter | NEW_BULK_MIN | 0 | 0
116 | 59 | Fan 13 Speed (rpm) | New architecture ABB Inverter | NEW_F_13 | 0 | 0
117 | 59 | Fan 14 Speed (rpm) | New architecture ABB Inverter | NEW_F_14 | 0 | 0
118 | 59 | Fan 15 Speed (rpm) | New architecture ABB Inverter | NEW_F_15 | 0 | 0
119 | 59 | Fan 16 Speed (rpm) | New architecture ABB Inverter | NEW_F_16 | 0 | 0
126 | 59 | Iac Max ( Calculated ) | New architecture ABB Inverter | NEW_IAC_MAX | 0 | 0
125 | 59 | Iac Min ( Calculated ) | New architecture ABB Inverter | NEW_IAC_MIN | 0 | 0
17 | 59 | Temporary Iac DCInj R | New architecture ABB Inverter | NEW_Idc1 | 0 | 0
18 | 59 | Temporary Iac DCInj S | New architecture ABB Inverter | NEW_Idc2 | 0 | 0
19 | 59 | Temporary Iac DCInj T | New architecture ABB Inverter | NEW_Idc3 | 0 | 0
135 | 59 | Dc Inject Max ( Calculated ) | New architecture ABB Inverter | NEW_IdcINJ_MAX | 0 | 0
160 | 59 | IGBT Temperature 1 (°C) | New architecture ABB Inverter | NEW_IGBT_T_1 | 0 | 0
160 | 59 | Tbst_B | TRIO-50.0 only | TRIO50_Tbst_B | 0 | 0
169 | 59 | IGBT Temperature 10 (°C) | New architecture ABB Inverter | NEW_IGBT_T_10 | 0 | 0
169 | 59 | Tcoil_1 | TRIO-50.0 only | TRIO50_Tcoil_1 | 0 | 0
170 | 59 | IGBT Temperature 11 (°C) | New architecture ABB Inverter | NEW_IGBT_T_11 | 0 | 0
170 | 59 | Tcoil_2 | TRIO-50.0 only | TRIO50_Tcoil_2 | 0 | 0
171 | 59 | IGBT Temperature 12 (°C) | New architecture ABB Inverter | NEW_IGBT_T_12 | 0 | 0
171 | 59 | Tbst_MAX | TRIO-50.0 only | TRIO50_Tbst_MAX | 0 | 0
172 | 59 | IGBT Temperature 13 (°C) | New architecture ABB Inverter | NEW_IGBT_T_13 | 0 | 0
172 | 59 | Tbst_MIN | TRIO-50.0 only | TRIO50_Tbst_MIN | 0 | 0
173 | 59 | IGBT Temperature 14 (°C) | New architecture ABB Inverter | NEW_IGBT_T_14 | 0 | 0
173 | 59 | Tinv_MAX | TRIO-50.0 only | TRIO50_Tinv_MAX | 0 | 0
174 | 59 | IGBT Temperature 15 (°C) | New architecture ABB Inverter | NEW_IGBT_T_15 | 0 | 0
174 | 59 | Tinv_MIN | TRIO-50.0 only | TRIO50_Tinv_MIN | 0 | 0
175 | 59 | IGBT Temperature 16 (°C) | New architecture ABB Inverter | NEW_IGBT_T_16 | 0 | 0
161 | 59 | IGBT Temperature 2 (°C) | New architecture ABB Inverter | NEW_IGBT_T_2 | 0 | 0
161 | 59 | Tbst_C | TRIO-50.0 only | TRIO50_Tbst_C | 0 | 0
162 | 59 | IGBT Temperature 3 (°C) | New architecture ABB Inverter | NEW_IGBT_T_3 | 0 | 0
162 | 59 | Tinv_S_top | TRIO-50.0 only | TRIO50_Tinv_S_top | 0 | 0
163 | 59 | IGBT Temperature 4 (°C) | New architecture ABB Inverter | NEW_IGBT_T_4 | 0 | 0
163 | 59 | Tinv_T_top | TRIO-50.0 only | TRIO50_Tinv_T_top | 0 | 0
164 | 59 | IGBT Temperature 5 (°C) | New architecture ABB Inverter | NEW_IGBT_T_5 | 0 | 0
164 | 59 | Tinv_R_bottom | TRIO-50.0 only | TRIO50_Tinv_R_bottom | 0 | 0
165 | 59 | IGBT Temperature 6 (°C) | New architecture ABB Inverter | NEW_IGBT_T_6 | 0 | 0
165 | 59 | Tinv_S_bottom | TRIO-50.0 only | TRIO50_Tinv_S_bottom | 0 | 0
166 | 59 | IGBT Temperature 7 (°C) | New architecture ABB Inverter | NEW_IGBT_T_7 | 0 | 0
166 | 59 | Tinv_T_bottom | TRIO-50.0 only | TRIO50_Tinv_T_bottom | 0 | 0
167 | 59 | IGBT Temperature 8 (°C) | New architecture ABB Inverter | NEW_IGBT_T_8 | 0 | 0
167 | 59 | Tmodule | TRIO-50.0 only | TRIO50_Tmodule | 0 | 0
168 | 59 | IGBT Temperature 9 (°C) | New architecture ABB Inverter | NEW_IGBT_T_9 | 0 | 0
168 | 59 | T_AC_box | TRIO-50.0 only | TRIO50_T_AC_box | 0 | 0
123 | 59 | Iin Max ( Calculated ) | New architecture ABB Inverter | NEW_IIN_MAX | 0 | 0
122 | 59 | Iin Min ( Calculated ) | New architecture ABB Inverter | NEW_IIN_MIN | 0 | 0
134 | 59 | Ileak Max ( Calculated ) New architecture | New architecture ABB Inverter | NEW_ILEAK_MAX | 0 | 0
137 | 59 | Over Temperature Max 3 ( Calculated ) | New architecture ABB Inverter | NEW_OVER_T_MAX | 0 | 0
136 | 59 | Over Temperature Max 2 ( Calculated ) | New architecture ABB Inverter | NEW_OVER_T_MIN | 0 | 0
71 | 59 | Pac phase r | New architecture ABB Inverter | NEW_P1 | 0 | 0
72 | 59 | Pac phase s | New architecture ABB Inverter | NEW_P2 | 0 | 0
73 | 59 | Pac phase t | New architecture ABB Inverter | NEW_P3 | 0 | 0
10 | 59 | Pin Tot | New architecture ABB Inverter | NEW_PinTot | 0 | 0
103 | 59 | Q Grid | New architecture ABB Inverter | NEW_QTot | 0 | 0
14 | 59 | Inverter Temperature R | New architecture ABB Inverter | NEW_T_R | 0 | 0
15 | 59 | Inverter Temperature S | New architecture ABB Inverter | NEW_T_S | 0 | 0
16 | 59 | Inverter Temperature T | New architecture ABB Inverter | NEW_T_T | 0 | 0
133 | 59 | Over Temperature Max 1 ( Calculated ) | New architecture ABB Inverter | NEW_UNDER_T_MAX | 0 | 0
132 | 59 | Under Temperature Min 1 ( Calculated ) | New architecture ABB Inverter | NEW_UNDER_T_MIN | 0 | 0
11 | 59 | Vac Internal R | New architecture ABB Inverter | NEW_URMS1 | 0 | 0
74 | 59 | Vac Not Avg phase r | New architecture ABB Inverter | NEW_URMS1_NOTAVG | 0 | 0
12 | 59 | Vac Internal S | New architecture ABB Inverter | NEW_URMS2 | 0 | 0
66 | 59 | Grid Voltage phase s (V) Read by DcDc | New architecture ABB Inverter | NEW_URMS2_DCDC | 0 | 0
75 | 59 | Vac Not Avg phase s | New architecture ABB Inverter | NEW_URMS2_NOTAVG | 0 | 0
113 | 59 | Grid peak voltage phase S [V] | New architecture ABB Inverter | NEW_URMS2_PEAK | 0 | 0
13 | 59 | Vac Internal T | New architecture ABB Inverter | NEW_URMS3 | 0 | 0
68 | 59 | Grid Voltage phase t (V) Read by DcDc | New architecture ABB Inverter | NEW_URMS3_DCDC | 0 | 0
76 | 59 | Vac Not Avg phase t | New architecture ABB Inverter | NEW_URMS3_NOTAVG | 0 | 0
114 | 59 | Grid peak voltage phase T [V] | New architecture ABB Inverter | NEW_URMS3_PEAK | 0 | 0
121 | 59 | Vin Max ( Calculated ) | New architecture ABB Inverter | NEW_VIN_MAX | 0 | 0
120 | 59 | Vin Min ( Calculated ) | New architecture ABB Inverter | NEW_VIN_MIN | 0 | 0
37 | 59 | Wind Generator Frequency (Hz) | New architecture ABB Inverter | NEW_WIND_G_FREQ | 0 | 0
144 | 59 | I Battery 1 ( Charger ) | New architecture ABB Inverter | STORAGE_IBAT_1 | 0 | 0
145 | 59 | I Battery 2 ( Charger ) | New architecture ABB Inverter | STORAGE_IBAT_2 | 0 | 0
146 | 59 | I Battery 3 ( Charger ) | New architecture ABB Inverter | STORAGE_IBAT_3 | 0 | 0
147 | 59 | I Battery 4 ( Charger ) | New architecture ABB Inverter | STORAGE_IBAT_4 | 0 | 0
188 | 59 | PAC total transferred from the grid (W) | New architecture ABB Inverter | STORAGE_PAC_FROM_GRID | 0 | 0
115 | 59 | Storage Pac Limited over Pac Max | New architecture ABB Inverter | STORAGE_PAC_LIM | 0 | 0
187 | 59 | PAC total transferred to the grid (W) | New architecture ABB Inverter | STORAGE_PAC_TO_GRID | 0 | 0
148 | 59 | P Battery 1 ( Charger ) | New architecture ABB Inverter | STORAGE_PBAT_1 | 0 | 0
149 | 59 | P Battery 2 ( Charger ) | New architecture ABB Inverter | STORAGE_PBAT_2 | 0 | 0
150 | 59 | P Battery 3 ( Charger ) | New architecture ABB Inverter | STORAGE_PBAT_3 | 0 | 0
151 | 59 | P Battery 4 ( Charger ) | New architecture ABB Inverter | STORAGE_PBAT_4 | 0 | 0
180 | 59 | Grid backup voltage phase R [V] | New architecture ABB Inverter | STORAGE_URMS1_BACKUP | 0 | 0
181 | 59 | Grid backup voltage phase S [V] | New architecture ABB Inverter | STORAGE_URMS2_BACKUP | 0 | 0
182 | 59 | Grid backup voltage phase T [V] | New architecture ABB Inverter | STORAGE_URMS3_BACKUP | 0 | 0
140 | 59 | V Battery 1 ( Charger ) | New architecture ABB Inverter | STORAGE_VBAT_1 | 0 | 0
141 | 59 | V Battery 2 ( Charger ) | New architecture ABB Inverter | STORAGE_VBAT_2 | 0 | 0
142 | 59 | V Battery 3 ( Charger ) | New architecture ABB Inverter | STORAGE_VBAT_3 | 0 | 0
143 | 59 | V Battery 4 ( Charger ) | New architecture ABB Inverter | STORAGE_VBAT_4 | 0 | 0
0 | 78 | Daily Energy E0 | Daily Energy | En_Day_E0 | 0 | 0
1 | 78 | Weekly Energy E0 | Weekly Energy | En_Wk_E0 | 0 | 0
2 | 78 | Not Used Energy E0 | Not Used Energy | En_NU_E0 | 0 | 0
3 | 78 | Montly Energy E0 | Montly Energy | En_Mont_E0 | 0 | 0
4 | 78 | Yearly Energy E0 | Yearly Energy | En_Year_E0 | 0 | 0
5 | 78 | Total Energy E0 | Total Energy | En_Tot_E0 | 0 | 0
6 | 78 | Partial Energy E0 | Partial Energy | En_Par_E0 | 0 | 0
100 | 78 | Daily Energy E1 | Daily Energy | En_Day_E1 | 0 | 0
101 | 78 | Weekly Energy E1 | Weekly Energy | En_Wk_E1 | 0 | 0
102 | 78 | Not Used Energy E1 | Not Used Energy | En_NU_E1 | 0 | 0
103 | 78 | Montly Energy E1 | Montly Energy | En_Mont_E1 | 0 | 0
104 | 78 | Yearly Energy E1 | Yearly Energy | En_Year_E1 | 0 | 0
105 | 78 | Total Energy E1 | Total Energy | En_Tot_E1 | 0 | 0
106 | 78 | Partial Energy E1 | Partial Energy | En_Par_E1 | 0 | 0
107 | 78 | Daily Energy E2 | Daily Energy | En_Day_E2 | 0 | 0
108 | 78 | Weekly Energy E2 | Weekly Energy | En_Wk_E2 | 0 | 0
109 | 78 | Not Used Energy E2 | Not Used Energy | En_NU_E2 | 0 | 0
110 | 78 | Montly Energy E2 | Montly Energy | En_Mont_E2 | 0 | 0
111 | 78 | Yearly Energy E2 | Yearly Energy | En_Year_E2 | 0 | 0
112 | 78 | Total Energy E2 | Total Energy | En_Tot_E2 | 0 | 0
113 | 78 | Partial Energy E2 | Partial Energy | En_Par_E2 | 0 | 0
114 | 78 | Daily Energy E3 | Daily Energy | En_Day_E3 | 0 | 0
115 | 78 | Weekly Energy E3 | Weekly Energy | En_Wk_E3 | 0 | 0
116 | 78 | Not Used Energy E3 | Not Used Energy | En_NU_E3 | 0 | 0
117 | 78 | Montly Energy E3 | Montly Energy | En_Mont_E3 | 0 | 0
118 | 78 | Yearly Energy E3 | Yearly Energy | En_Year_E3 | 0 | 0
119 | 78 | Total Energy E3 | Total Energy | En_Tot_E3 | 0 | 0
120 | 78 | Partial Energy E3 | Partial Energy | En_Par_E3 | 0 | 0
121 | 78 | Daily Energy E4 | Daily Energy | En_Day_E4 | 0 | 0
122 | 78 | Weekly Energy E4 | Weekly Energy | En_Wk_E4 | 0 | 0
123 | 78 | Not Used Energy E4 | Not Used Energy | En_NU_E4 | 0 | 0
124 | 78 | Montly Energy E4 | Montly Energy | En_Mont_E4 | 0 | 0
125 | 78 | Yearly Energy E4 | Yearly Energy | En_Year_E4 | 0 | 0
126 | 78 | Total Energy E4 | Total Energy | En_Tot_E4 | 0 | 0
127 | 78 | Partial Energy E4 | Partial Energy | En_Par_E4 | 0 | 0
128 | 78 | Daily Energy E5 | Daily Energy | En_Day_E5 | 0 | 0
129 | 78 | Weekly Energy E5 | Weekly Energy | En_Wk_E5 | 0 | 0
130 | 78 | Not Used Energy E5 | Not Used Energy | En_NU_E5 | 0 | 0
131 | 78 | Montly Energy E5 | Montly Energy | En_Mont_E5 | 0 | 0
132 | 78 | Yearly Energy E5 | Yearly Energy | En_Year_E5 | 0 | 0
133 | 78 | Total Energy E5 | Total Energy | En_Tot_E5 | 0 | 0
134 | 78 | Partial Energy E5 | Partial Energy | En_Par_E5 | 0 | 0
135 | 78 | Daily Energy E6 | Daily Energy | En_Day_E6 | 0 | 0
136 | 78 | Weekly Energy E6 | Weekly Energy | En_Wk_E6 | 0 | 0
137 | 78 | Not Used Energy E6 | Not Used Energy | En_NU_E6 | 0 | 0
138 | 78 | Montly Energy E6 | Montly Energy | En_Mont_E6 | 0 | 0
139 | 78 | Yearly Energy E6 | Yearly Energy | En_Year_E6 | 0 | 0
140 | 78 | Total Energy E6 | Total Energy | En_Tot_E6 | 0 | 0
141 | 78 | Partial Energy E6 | Partial Energy | En_Par_E6 | 0 | 0
142 | 78 | Daily Energy E7 | Daily Energy | En_Day_E7 | 0 | 0
143 | 78 | Weekly Energy E7 | Weekly Energy | En_Wk_E7 | 0 | 0
144 | 78 | Not Used Energy E7 | Not Used Energy | En_NU_E7 | 0 | 0
145 | 78 | Montly Energy E7 | Montly Energy | En_Mont_E7 | 0 | 0
146 | 78 | Yearly Energy E7 | Yearly Energy | En_Year_E7 | 0 | 0
147 | 78 | Total Energy E7 | Total Energy | En_Tot_E7 | 0 | 0
148 | 78 | Partial Energy E7 | Partial Energy | En_Par_E7 | 0 | 0
149 | 78 | Daily Energy E8 | Daily Energy | En_Day_E8 | 0 | 0
150 | 78 | Weekly Energy E8 | Weekly Energy | En_Wk_E8 | 0 | 0
151 | 78 | Not Used Energy E8 | Not Used Energy | En_NU_E8 | 0 | 0
152 | 78 | Montly Energy E8 | Montly Energy | En_Mont_E8 | 0 | 0
153 | 78 | Yearly Energy E8 | Yearly Energy | En_Year_E8 | 0 | 0
154 | 78 | Total Energy E8 | Total Energy | En_Tot_E8 | 0 | 0
155 | 78 | Partial Energy E8 | Partial Energy | En_Par_E8 | 0 | 0
156 | 78 | Daily Energy E9 | Daily Energy | En_Day_E9 | 0 | 0
157 | 78 | Weekly Energy E9 | Weekly Energy | En_Wk_E9 | 0 | 0
158 | 78 | Not Used Energy E9 | Not Used Energy | En_NU_E9 | 0 | 0
159 | 78 | Montly Energy E9 | Montly Energy | En_Mont_E9 | 0 | 0
160 | 78 | Yearly Energy E9 | Yearly Energy | En_Year_E9 | 0 | 0
161 | 78 | Total Energy E9 | Total Energy | En_Tot_E9 | 0 | 0
162 | 78 | Partial Energy E9 | Partial Energy | En_Par_E9 | 0 | 0
163 | 78 | Daily Energy E10 | Daily Energy | En_Day_E10 | 0 | 0
164 | 78 | Weekly Energy E10 | Weekly Energy | En_Wk_E10 | 0 | 0
165 | 78 | Not Used Energy E10 | Not Used Energy | En_NU_E10 | 0 | 0
166 | 78 | Montly Energy E10 | Montly Energy | En_Mont_E10 | 0 | 0
167 | 78 | Yearly Energy E10 | Yearly Energy | En_Year_E10 | 0 | 0
168 | 78 | Total Energy E10 | Total Energy | En_Tot_E10 | 0 | 0
169 | 78 | Partial Energy E10 | Partial Energy | En_Par_E10 | 0 | 0
170 | 78 | Daily Energy E11 | Daily Energy | En_Day_E11 | 0 | 0
171 | 78 | Weekly Energy E11 | Weekly Energy | En_Wk_E11 | 0 | 0
172 | 78 | Not Used Energy E11 | Not Used Energy | En_NU_E11 | 0 | 0
173 | 78 | Montly Energy E11 | Montly Energy | En_Mont_E11 | 0 | 0
174 | 78 | Yearly Energy E11 | Yearly Energy | En_Year_E11 | 0 | 0
175 | 78 | Total Energy E11 | Total Energy | En_Tot_E11 | 0 | 0
176 | 78 | Partial Energy E11 | Partial Energy | En_Par_E11 | 0 | 0
177 | 78 | Daily Energy E12 | Daily Energy | En_Day_E12 | 0 | 0
178 | 78 | Weekly Energy E12 | Weekly Energy | En_Wk_E12 | 0 | 0
179 | 78 | Not Used Energy E12 | Not Used Energy | En_NU_E12 | 0 | 0
180 | 78 | Montly Energy E12 | Montly Energy | En_Mont_E12 | 0 | 0
181 | 78 | Yearly Energy E12 | Yearly Energy | En_Year_E12 | 0 | 0
182 | 78 | Total Energy E12 | Total Energy | En_Tot_E12 | 0 | 0
183 | 78 | Partial Energy E12 | Partial Energy | En_Par_E12 | 0 | 0
184 | 78 | Daily Energy E13 | Daily Energy | En_Day_E13 | 0 | 0
185 | 78 | Weekly Energy E13 | Weekly Energy | En_Wk_E13 | 0 | 0
186 | 78 | Not Used Energy E13 | Not Used Energy | En_NU_E13 | 0 | 0
187 | 78 | Montly Energy E13 | Montly Energy | En_Mont_E13 | 0 | 0
188 | 78 | Yearly Energy E13 | Yearly Energy | En_Year_E13 | 0 | 0
189 | 78 | Total Energy E13 | Total Energy | En_Tot_E13 | 0 | 0
190 | 78 | Partial Energy E13 | Partial Energy | En_Par_E13 | 0 | 0
191 | 78 | Daily Energy E14 | Daily Energy | En_Day_E14 | 0 | 0
192 | 78 | Weekly Energy E14 | Weekly Energy | En_Wk_E14 | 0 | 0
193 | 78 | Not Used Energy E14 | Not Used Energy | En_NU_E14 | 0 | 0
194 | 78 | Montly Energy E14 | Montly Energy | En_Mont_E14 | 0 | 0
195 | 78 | Yearly Energy E14 | Yearly Energy | En_Year_E14 | 0 | 0
196 | 78 | Total Energy E14 | Total Energy | En_Tot_E14 | 0 | 0
197 | 78 | Partial Energy E14 | Partial Energy | En_Par_E14 | 0 | 0
198 | 78 | Daily Energy E15 | Daily Energy | En_Day_E15 | 0 | 0
199 | 78 | Weekly Energy E15 | Weekly Energy | En_Wk_E15 | 0 | 0
200 | 78 | Not Used Energy E15 | Not Used Energy | En_NU_E15 | 0 | 0
201 | 78 | Montly Energy E15 | Montly Energy | En_Mont_E15 | 0 | 0
202 | 78 | Yearly Energy E15 | Yearly Energy | En_Year_E15 | 0 | 0
203 | 78 | Total Energy E15 | Total Energy | En_Tot_E15 | 0 | 0
204 | 78 | Partial Energy E15 | Partial Energy | En_Par_E15 | 0 | 0
200 | 59 | Daily Self-Consumption | Daily Self-Consumption | SC_Day | 0 | 0
201 | 59 | Total Self-Consumption | Total Self-Consumption | SC_Tot | 0 | 0
202 | 59 | Daily Self-Sufficiency | Daily Self-Sufficiency | SS_Day | 0 | 0
203 | 59 | Total Self-Sufficiency | Total Self-Sufficiency | SS_Tot | 0 | 0
210 | 59 | Input 3 Voltage (V) | New architecture ABB Inverter | AUR_UDC3 | 0 | 0
211 | 59 | Input 3 Current (A) | New architecture ABB Inverter | AUR_IDC3 | 0 | 0
212 | 59 | Input 3 Power (W) | New architecture ABB Inverter | AUR_PDC3 | 0 | 0
56 | 146 | I_Leakage | New architecture ABB Inverter | PCOM_B_ILEAK | 66 | 1
57 | 146 | I_Leakage_Filt | New architecture ABB Inverter | PCOM_B_ILEAK_FILT | 66 | 1
58 | 146 | I_Leakage_AVG | New architecture ABB Inverter | PCOM_B_ILEAK_AVG | 66 | 1
59 | 146 | I_Leakage_Res | New architecture ABB Inverter | PCOM_B_ILEAK_RES | 66 | 1
60 | 146 | DC Injection_R | New architecture ABB Inverter | AUR_Idc1 | 66 | 1
61 | 146 | DC Injection_S | New architecture ABB Inverter | AUR_Idc2 | 66 | 1
62 | 146 | DC Injection_T | New architecture ABB Inverter | AUR_Idc3 | 66 | 1
213 | 59 | Input 4 Voltage | New architecture ABB Inverter | AUR_UDC4 | 0 | 0
214 | 59 | Input 4 Current | New architecture ABB Inverter | AUR_IDC4 | 0 | 0
215 | 59 | Input 4 Power | New architecture ABB Inverter | AUR_PDC4 | 0 | 0
216 | 59 | Input 5 Voltage | New architecture ABB Inverter | AUR_UDC5 | 0 | 0
217 | 59 | Input 5 Current | New architecture ABB Inverter | AUR_IDC5 | 0 | 0
218 | 59 | Input 5 Power | New architecture ABB Inverter | AUR_PDC5 | 0 | 0
251 | 59 | Input 6 Voltage | New architecture ABB Inverter | AUR_UDC6 | 0 | 0
252 | 59 | Input 6 Current | New architecture ABB Inverter | AUR_IDC6 | 0 | 0
253 | 59 | Input 6 Power | New architecture ABB Inverter | AUR_PDC6 | 0 | 0
193 | 59 | IGBT Temperature 18 (°C) | PVS-120(100)-TL | NEW_IGBT_T_18 | 0 | 0
192 | 59 | IGBT Temperature 17 (°C) | PVS-120(100)-TL | NEW_IGBT_T_17 | 0 | 0
194 | 59 | IGBT Temperature 19 (°C) | PVS-120(100)-TL | NEW_IGBT_T_19 | 0 | 0
195 | 59 | IGBT Temperature 20 (°C) | PVS-120(100)-TL | NEW_IGBT_T_20 | 0 | 0
196 | 59 | IGBT Temperature 21 (°C) | PVS-120(100)-TL | NEW_IGBT_T_21 | 0 | 0
197 | 59 | IGBT Temperature 22 (°C) | PVS-120(100)-TL | NEW_IGBT_T_22 | 0 | 0
198 | 59 | IGBT Temperature 23 (°C) | PVS-120(100)-TL | NEW_IGBT_T_23 | 0 | 0
199 | 59 | IGBT Temperature 24 (°C) | PVS-120(100)-TL | NEW_IGBT_T_24 | 0 | 0
204 | 59 | IGBT Temperature 25 (°C) | PVS-120(100)-TL | NEW_IGBT_T_25 | 0 | 0
254 | 59 | Volt after LP filter in input of Volt-Watt function. | New architecture ABB Inverter | VW_Voltage_LP_filter | 0 | 0
384 | 146 | Frequency after LP filter in input of Freq.-Watt function. | New architecture ABB Inverter | FW_Frequency_LP_filter | 66 | 1
255 | 59 | Volt after LP filter in input of Volt-Var function. | New architecture ABB Inverter | VV_Voltage_LP_filter | 0 | 0
Inf | 56 | Read Var Micro | All | X | 0 | 0
inf | 130 | Read Var DSP | All | X | 0 | 0
Note on F1: A - DC/DC controller - 65 B - DC/AC controller - 66 H - Battery charger controller - 72 Y - Safety controller - 89
Note on G1: 0 - States 1 - Measures 2 - Parameters (configuration) 3 - Parameters (run-time) 4 - Operative command values 15 - Debug command values 100 - ID table data (by node ID) 101 - ID table data (by table index)

## grid_tied_var_tables
id | var_type | desc | var_unit | var_conversion | var_note
0 | I | 0: DC injection threshold (HIGH) | --- | REAL_Value = VAR_Value
1 | I | Inverter FW version (official) | --- | REAL_Value = VAR_Value | Usally expressed as a 4 chars string (ex. "B000")
2 | I | Pulse amplitude [A] (1-phase) / Reactive power % (3-phase) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_IOUT)
3 | I | Bulk voltage set-point (inverter) [V] (read-only) | V | REAL_Value = ((VAR_Value / (2^13)) x FS_VBULK) | Bulk ref. is usually managed internally by Supervisor
4 | I | 4: Pulse enable | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
5 | I | 5: BYTE_L = Delta F enable / BYTE_H = Wind frequency buffer size | --- | REAL_Value = VAR_Value | The BYTE_L is the F derivate enable The BYTE_H is the wind frequency buffer size
6 | I | Received parameters flag | --- | REAL_Value = VAR_Value | Set to 1 by DSP when all the parameters are received successfully
7 | I | 7: Max Active IAC [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_IOUT)
8 | I | 8: Grid standard (read-only) | --- | REAL_Value = VAR_Value | Grid-standard codes are described in "Aurora Communication Protocol" (CMD 58)
9 | I | 9: U >> Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
10 | I | 10: U > 10 min Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
11 | I | 11: U << Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
12 | I | 12: Max PAC [W] (read-only) | W | REAL_Value = VAR_Value | This VAR is also used for Derating and Power reduction
13 | I | ENEL autotest selection/enable | --- | REAL_Value = VAR_Value
14 | I | 14: Nominal Active PAC [W] | W | REAL_Value = VAR_Value
15 | I | 15: Reconn. time after grid fault [s] | s | REAL_Value = VAR_Value
16 | I | Impedance variation threshold | --- | REAL_Value = VAR_Value
17 | I | 17: F > Limit [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
18 | I | 18: F < Limit [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
19 | I | 19: Anti islanding period [ms] | ms | REAL_Value = VAR_Value
20 | I | VgSumMax [W] | --- | REAL_Value = VAR_Value
21 | I | Impedance variation value | --- | REAL_Value = VAR_Value
22 | I | Grid impedance | --- | REAL_Value = VAR_Value
23 | I | 23: U < Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
24 | I | 24: U > Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
25 | I | Grid fault reason | --- | REAL_Value = VAR_Value
26 | I | 26: MPPT type (read-only) | --- | REAL_Value = VAR_Value
27 | I | Time for the next connection | s | REAL_Value = VAR_Value | Set by DSP during connection sequence
28 | I | Inverter FW version (sub) | --- | REAL_Value = VAR_Value | Usally expressed as a 4 chars string (ex. "B000")
29 | I | K VAC (phase R) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
30 | I | Output relay selftest initialization/enable | --- | REAL_Value = VAR_Value
31 | I | 31: Max Reactive IAC [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_IOUT)
32 | I | PAC ramp | W/s | REAL_Value = (VAR_Value x 10)
33 | I | ENEL autotest result (measure) | V or Hz | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT) for OV/UV tests REAL_Value = (2500000 / VAR_Value) for OF/UF tests
34 | I | 34: 3-wire / 4-wire mode (3-phase) |  | REAL_Value = VAR_Value
35 | I | 35: DC injection threshold (LOW) | --- | REAL_Value = VAR_Value
36 | I | DC injection value (phase R) | mA??? | REAL_Value = VAR_Value
37 | I | ENEL autotest result (trip time) | ms | REAL_Value = VAR_Value
38 | I | 38: Time for conn. after non-grid prot. [s] | s | REAL_Value = VAR_Value
39 | I | 39: MIN FAC (before connection) [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
40 | I | Q VAC (phase R) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
41 | I | K Vneutral (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
42 | I | Q Vneutral (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
43 | I | Inverter model code (read-only) | VA | REAL_Value = VAR_Value
44 | I | 44: Soglia attivazione LVRT [V] | V | REAL_Value = VAR_Value
45 | I | K VAC (phase S) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
46 | I | Q VAC (phase S) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
47 | I | K VAC (phase T) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
48 | I | Q VAC (phase T) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
49 | I | 49: Max total IAC [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_IOUT)
50 | I | 50: Output Overcurrent [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_IOUT)
51 | I | MaxAVG: B_H = N Cyc/ B_L = Buffer Size | --- | REAL_Value = VAR_Value
52 | I | MaxAVG: B_H RestoreSlope%Pmax/min;B_L[4:7]DeltaVReg;[3:0]DeltaVRestorePower | --- | REAL_Value = VAR_Value
53 | I | K IAC (phase R) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
54 | I | Q IAC (phase R) (calibration) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_IOUT)
55 | I | K IAC (phase S) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
56 | I | Q IAC (phase S) (calibration) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_IOUT)
57 | I | K IAC (phase T) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
58 | I | Q IAC (phase T) (calibration) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_IOUT)
59 | I | K VBULK (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
60 | I | Q VBULK (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VBULK)
61 | I | 61: Max Q [var] | VAR | REAL_Value = VAR_Value | This VAR is also used for reactive power derating
62 | I | 62: Time end Frequency Derating [s] | s | REAL_Value = VAR_Value
63 | I | 63: Output capacitor [nF] | nF | REAL_Value = VAR_Value
64 | I | 64: Anti-islanding % | --- | REAL_Value = ((VAR_Value / (2^15)) x 100)
65 | I | 65:Max delta T (threshold for Freq Drift) [usec] | --- | REAL_Value = VAR_Value
66 | I | DC injection value (phase S) | mA??? | REAL_Value = VAR_Value
67 | I | K Max delta cycle | mA??? | REAL_Value = VAR_Value
68 | I | 68: Max delta cycle | --- | REAL_Value = VAR_Value
69 | I | Reactive Power for Passive A.I. [Var] | mA??? | REAL_Value = VAR_Value
70 | I | B_H =Fix Chopping factor [mHz] B_L = Kp Drift Reg. | mA??? | REAL_Value = VAR_Value
71 | I | B_H= Delta Freq x PLL error incr. B_L= Delta Freq x Active A.I. detection | mA??? | REAL_Value = VAR_Value
72 | I | 72: U>> limit (ph-ph) [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
73 | I | 73: U<< limit (ph-ph) [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
74 | I | 74: (DeltaP / Hz) for OF derating [%Pist/(100*Hz)] | --- | REAL_Value = (VAR_Value / (2^15))
75 | I | 75: Min VGSUM POW (3-phase) [W] | --- | REAL_Value = VAR_Value
76 | I | 76: U< limit (ph-ph) [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
77 | I | 77: U> limit (ph-ph) [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
78 | I | 78: FLT FFWD enable + Delat Freq | --- | REAL_Value = VAR_Value
79 | I | 79: MAX VAC (before connection) [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
80 | I | COS-PHI % ??? | --- | REAL_Value = VAR_Value
81 | I | 81: VAC peak OV threshold [V] | V | REAL_Value = VAR_Value
82 | I | BDEW mode enable | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
83 | I | BDEW smooth | --- | REAL_Value = VAR_Value
84 | I | 84: Soglia esportazione max pow per fault symm [V] | V | REAL_Value = VAR_Value
85 | I | 85: BYTE_H = Frequency buffer size / BYTE_L = OF derating mode | --- | REAL_Value = VAR_Value | The BYTE_L is the mode: 0=Disabled - 1=BDEW - 2=VDE-AR-N - 3=CEI The BYTE_H is the size of the frequency buffer (1-255)
86 | I | 86: Min/max attenuation factor | --- | REAL_Value = (VAR_Value / (2^14))
87 | I | 87: U < protection time [ms] | ms | REAL_Value = VAR_Value | 1=Disabled - 0=Enabled
88 | I | 88: U >> protection time [ms] | ms | REAL_Value = VAR_Value | (initially used only for BDEW standard) - (ammisible range 0-65535 ms)
89 | I | 89: U << protection time [ms] | ms | REAL_Value = VAR_Value | (initially used only for BDEW standard) - (ammisible range 0-65535 ms)
90 | I | 90: U > protection time [ms] | ms | REAL_Value = VAR_Value | (initially used only for BDEW standard) - (ammisible range 0-65535 ms)
91 | I | 91: Min Vbulk UV [V] (read-only) | V | REAL_Value = VAR_Value
92 | I | 92: K retta reattiva in LVRT | --- | REAL_Value = (VAR_Value / (2^13))
93 | I | 93: Slow Ramp Function | --- | REAL_Value = VAR_Value | The BYTE_L holds the slow ramp enable flags: - Bit0 = General enable - Bit1 = SRE always - Bit2 = SRE after grid-fail - Bit3 = SRE after OF derating The BYTE_H is the slow ramp slew-rate [P%/min - 1-100]
94 | I | 94: MIN VAC (before connection): UV threshold before connection [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
95 | I | 95: MAX FAC (before connection) + Rientro da derating in frequenza [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
96 | I | 96: Soglia attivazione derating in frequenza [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
97 | I | 97: F > protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
98 | I | 98: F < protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
99 | I | 99: DC injection protection buffer size BYTE_H / BYTE_L for HIGH / LOW threshold | ms | REAL_Value = VAR_Value | The BYTE_L is the prot.buffer size for the LOW DC injection threshold The BYTE_H is the prot. buffer size for the HIGH DC injection threshold
100 | B | NOT USED | --- | --- | ---
101 | B | Booster FW version (official) | --- | REAL_Value = VAR_Value | Usally expressed as a 4 chars string (ex. "A000")
102 | B | Step duty MPPT | --- | REAL_Value = VAR_Value
103 | B | Time MPPT | s | REAL_Value = VAR_Value
104 | B | Power measure period | --- | REAL_Value = VAR_Value
105 | B | Input mode (read-only) | --- | REAL_Value = VAR_Value | 0=INDEPENDENT - 1=PARALLEL NOTE: Var. 105 can become free if var. 211 is used instead.
106 | B | Received parameters flag | --- | REAL_Value = VAR_Value | Set to 1 by DSP when all the parameters are received successfully
107 | B | Bulk reference value | V | REAL_Value = ((VAR_Value / (2^13)) x FS_VBULK) | Bulk ref. is usually managed internally by Supervisor
108 | B | 108: Grid standard (read-only) | --- | REAL_Value = VAR_Value | Grid-standard codes are described in "Aurora Communication Protocol"
109 | B | 109: Input power limitation [W] (read-only) | W | REAL_Value = ((VAR_Value / (2^15)) x FS_VIN x FS_IIN)
110 | B | Booster FW version (sub) | --- | REAL_Value = VAR_Value | Usally expressed as a 4 chars string (ex. "A000")
111 | B | 111: U >> Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
112 | B | 112: U << Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
113 | B | Impedance variation threshold | --- | REAL_Value = VAR_Value
114 | B | 114: F >> Limit [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
115 | B | 115: F << Limit [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
116 | B | Grid fault reason | --- | REAL_Value = VAR_Value
117 | B | Impedance variation vale | --- | REAL_Value = VAR_Value
118 | B | Average impedance value | --- | REAL_Value = VAR_Value
119 | B | Output relay selftest enable | --- | REAL_Value = VAR_Value
120 | B | Output relay selftest selection | --- | REAL_Value = VAR_Value
121 | B | Grid impedance | --- | REAL_Value = VAR_Value
122 | B | Pulse enable | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
123 | B | 123: U < Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
124 | B | 124: U > Limit [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
125 | B | 125: V-Start channel 2 [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VIN)
126 | B | F derivate enable | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
127 | B | Offset on max threshold | --- | REAL_Value = VAR_Value
128 | B | Multi-Max scan enable | --- | REAL_Value = VAR_Value | Scan is usually managed internally by Supervisor
129 | B | Booster model code (read-only) | --- | REAL_Value = VAR_Value | Free vars after MCU "vars sharing" (but only for newer models)
130 | B | 130: V-Start channel 1 [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VIN)
131 | B | K VAC (phase R) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
132 | B | Q VAC (phase R) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
133 | B | K Iin CH. 1 (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
134 | B | Q Iin CH. 1 (calibration) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_Iin)
135 | B | K Iin CH. 2 (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
136 | B | Q Iin CH. 2 (calibration) | A | REAL_Value = ((VAR_Value / (2^15)) x FS_Iin)
137 | B | Constant Vin value | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VIN)
138 | B | Constant Vin enable | --- | REAL_Value = VAR_Value
139 | B | 139: UV protection time [s] | s | REAL_Value = VAR_Value
140 | B | 140: 3-wire/4-wire mode | --- | REAL_Value = VAR_Value | 3=3-wire - 4=4-wire
141 | B | K VAC (phase S) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
142 | B | Q VAC (phase S) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
143 | B | K VAC (phase T) (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
144 | B | Q VAC (phase T) (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
145 | B | K VBULK (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
146 | B | Q VBULK (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VBULK)
147 | B | K Vin CH. 1 (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
148 | B | Q Vin CH. 1 (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_Vin)
149 | B | K Vin CH. 2 (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
150 | B | Q Vin CH. 2 (calibration) | V | REAL_Value = ((VAR_Value / (2^15)) x FS_Vin)
151 | B | 151: MPPT min max | --- | REAL_Value = VAR_Value
152 | B | 152: MPPT KI | --- | REAL_Value = (VAR_Value / 16)
153 | B | 153: MPPT amplitude | V | REAL_Value = (VAR_Value / 10)
154 | B | Multi-Max scan pre-enable | --- | REAL_Value = VAR_Value | Scan is usually managed internally by Supervisor
155 | B | Multi-Max scan MIN Vin CH. 1 | V | REAL_Value = (VAR_Value / 16)
156 | B | Multi-Max scan TOP Vin CH. 1 | V | REAL_Value = VAR_Value
157 | B | Multi-Max scan MIN Vin CH. 2 | V | REAL_Value = VAR_Value
158 | B | Multi-Max scan TOP Vin CH. 2 | V | REAL_Value = VAR_Value
159 | B | Max leakage current (booster) [mA] | mA | REAL_Value = VAR_Value
160 | B | Power saving channel selection | --- | REAL_Value = VAR_Value | Power saving channel selection is usually managed internally by Supervisor
161 | B | 161: MPPT KP | --- | REAL_Value = (VAR_Value / (2^15))
162 | B | 162: BYTE_H = Frequency buffer size / BYTE_L = Freq protection disable | --- | REAL_Value = VAR_Value | The BYTE_L is the disable flag: 0=Enabled - 1=Disabled The BYTE_H is the size of the frequency buffer (1-255)
163 | B | 163: Coils ratio (Read Only) | --- | REAL_Value = (VAR_Value / (2^14))
164 | B | 164: Bulk OV threshold [V] (read only) | V | REAL_Value = VAR_Value
165 | B | 165: U >> protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
166 | B | 166: U << protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
167 | B | 167: F >> protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
168 | B | 168: F << protection time [ms] | ms | REAL_Value = VAR_Value | (ammisible range 0-65535 ms)
169 | B | 169: Max Input current x channel [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_Iin) | ---
170 | B | 170: Input overcurrent x channel [A] | A | REAL_Value = ((VAR_Value / (2^14)) x FS_Iin) | ---
171 | B | NOT USED | --- | --- | ---
172 | B | NOT USED | --- | --- | ---
173 | B | NOT USED | --- | --- | ---
174 | B | NOT USED | --- | --- | ---
175 | B | NOT USED | --- | --- | ---
176 | B | NOT USED | --- | --- | ---
177 | B | NOT USED | --- | --- | ---
178 | B | NOT USED | --- | --- | ---
179 | B | NOT USED | --- | --- | ---
180 | B | NOT USED | --- | --- | ---
181 | B | NOT USED | --- | --- | ---
182 | B | NOT USED | --- | --- | ---
183 | B | NOT USED | --- | --- | ---
184 | B | NOT USED | --- | --- | ---
185 | B | NOT USED | --- | --- | ---
186 | B | NOT USED | --- | --- | ---
187 | B | NOT USED | --- | --- | ---
188 | B | NOT USED | --- | --- | ---
189 | B | NOT USED | --- | --- | ---
190 | B | NOT USED | --- | --- | ---
191 | B | NOT USED | --- | --- | ---
192 | B | NOT USED | --- | --- | ---
193 | B | NOT USED | --- | --- | ---
194 | B | NOT USED | --- | --- | ---
195 | B | NOT USED | --- | --- | ---
196 | B | NOT USED | --- | --- | ---
197 | B | NOT USED | --- | --- | ---
198 | B | NOT USED | --- | --- | ---
199 | B | NOT USED | --- | --- | ---
200 | S | 200: "is amorphous" flag | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
201 | S/I/B | 201: Nominal VAC [V] | V | REAL_Value = ((VAR_Value / (2^15)) x FS_VOUT)
202 | S/I/B | 202: Nominal FAC [Hz] | Hz | REAL_Value = (2500000 / VAR_Value)
203 | S | Clock state | --- | REAL_Value = VAR_Value | Clock state is usually managed internally by Supervisor
204 | S | Derating mode | --- | REAL_Value = VAR_Value
205 | S | K IAC (calibration) (OLD)??? | --- | REAL_Value = (VAR_Value / (2^14))
206 | S | Q IAC (calibration) (OLD)??? | A | REAL_Value = ((VAR_Value / (2^15)) x FS_IOUT)
207 | S/I | K PAC (calibration) | --- | REAL_Value = (VAR_Value / (2^13))
208 | S/I | Q PAC (calibration) | W | REAL_Value = VAR_Value
209 | S | PAC calibration enable | --- | REAL_Value = VAR_Value | 0=Enabled - 1=Disabled
210 | S | 210: RS485 baud-rate code | --- | REAL_Value = VAR_Value
211 | S | 211: Input mode (read-only) | --- | REAL_Value = VAR_Value | The BYTE_L is the input mode The BYTE_H is the HW configuration bits field
212 | S | 212: R-iso measure disable | --- | REAL_Value = VAR_Value | 0=Enabled - 1=Disabled
213 | S | 213: Remote mode | --- | REAL_Value = VAR_Value
214 | S | 214: Fan mounted | --- | REAL_Value = VAR_Value
215 | S/I/B | 215: "Who am I" model code (change also var. 12, 43, 109, 129) | --- | REAL_Value = VAR_Value | Model codes are described in "Aurora Communication Protocol" (CMD 58)
216 | S | Last alarm-state | --- | REAL_Value = VAR_Value | Alarm states are described in "Aurora Communication Protocol" (CMD 50)
217 | S | 217: Digital alarm mode | --- | REAL_Value = VAR_Value
218 | S | 218: "is wind" flag | --- | REAL_Value = VAR_Value | 0=Solar - 1=Wind
219 | S | Is split? | --- | REAL_Value = VAR_Value
220 | S | 220: "is multi-max scan enabled" flag | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
221 | S | 221: Multi-max scan timeout [s] | s | REAL_Value = VAR_Value
222 | S | 222: R-ISO delay [s] | --- | REAL_Value = VAR_Value | For the "european" HW of isolated family is the time threshold for GF for floating GND
223 | S | 223: R-ISO threshold [Mohm] | Mohm | REAL_Value = ((VAR_Value / (2^15)) x FS_RISO)
224 | S | Power saving enable | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
225 | S | Grounding mode | --- | REAL_Value = VAR_Value
226 | S | 226: 110% / 100% PAC limitation selection [%W] | --- | REAL_Value = VAR_Value
227 | S | 227: Byte_L="is country selector timeout enable" flag / Byte_H="is country selector frozen" flag | --- | REAL_Value = VAR_Value | The BYTE_L is the country selection timeout enable (0 = Timeout disabled - 1 = Timeout enabled) The BYTE_H is the country selection freeze enable (0 = Selection free - 1 = Selection frozen)
228 | S/I/B | 228: Max Vbulk ref. [V] (read-only) | V | REAL_Value = VAR_Value
229 | S | GFI type | --- | REAL_Value = VAR_Value
230 | S | Is string selftest check enabled? | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
231 | S | 231: "is cos-phi/tan-phi sign inverted" flag | --- | REAL_Value = VAR_Value | 0=Disabled - 1=Enabled
232 | S | 232: Kcos-phi (calibration) | --- | REAL_Value = (VAR_Value / (2^14))
233 | S | 233: Qcos-phi (calibration) | --- | REAL_Value = (VAR_Value / (2^15))
234 | S | 234: % Vout_nom for lock-in (cos-phi = f(P)) [%V] | --- | REAL_Value = (VAR_Value / (2^15)) | If value = 0 the lock-in function is not used
235 | S | 235: % Vout_nom for lock-out (cos-phi = f(P)) [%V] | --- | REAL_Value = (VAR_Value / (2^15)) | If value = 0 the lock-out function is not used
236 | S | 236: % Pout_nom for lock-in (Q(U) mode) [%W] | --- | REAL_Value = (VAR_Value / (2^15)) | If value = 0 the lock-in function is not used
237 | S | 237: % Pout_nom for lock-out (Q(U) mode) [%W] | --- | REAL_Value = (VAR_Value / (2^15)) | If value = 0 the lock-out function is not used
238 | S | 238: % Pout_max for power reduction applied permanently [%W] | --- | REAL_Value = (VAR_Value / (2^15)) | Pout_max is the effective Pout_limit applied on var. 12
239 | S | 239: Byte H AUTOTEST Enable, Byte L AUTOTEST Timeout x10sec | s | REAL_Value = VAR_Value | The BYTE_L is the autotest timeout expressed in 10 s (10-2550 s) The BYTE_H is the autotest enable (0 = Test disabled - 1 = Test enabled)
240 | S | 240: MIN VAC for FAC protection disable [V] | V | REAL_Value = VAR_Value
241 | S | 241: Grid protection disable flags | --- | REAL_Value = VAR_Value | The BYTE_L holds the BOOSTER grid protection disable flags The BYTE_H holds the INVERTER grid protection disable flags
242 | S | Sleep-mode | --- | REAL_Value = VAR_Value | 0=AC standby feed with timeout (5 min) - 1=AC standby feed always
243 | S | Pseudo calibration cos-phi+ K | --- | TBD | For "old" 1-phase models only!!!
244 | S | Pseudo calibration cos-phi- K | --- | TBD | For "old" 1-phase models only!!!
245 | S | Pseudo calibration cos-phi+ Q | --- | TBD | For "old" 1-phase models only!!!
246 | S | Pseudo calibration cos-phi- Q | --- | TBD | For "old" 1-phase models only!!!
247 | S | Virtual KCC | --- | TBD | For "old" 1-phase models only!!!
248 | S | Vgnd threshold (LOW) | V | REAL_Value = VAR_Value
249 | S | Umax | V | TBD | 3G83 ( Slovenia )
250 | S | Umin | V | TBD | 3G83 ( Slovenia )
251 | S | 251: Qmax/Pnom | --- | same as var. 80
252 | S | Max number of leak fault events | --- | --- | ---
253 | S | OF derating STOP [Hz] | --- | --- | ---
254 | S | AFD management enable | --- | --- | ---
255 | S | NOT USED | --- | --- | ---

## variable
Id | Id_MSB | Id_LSB | Name | Unit | Type
0 | 0 | 0 | STRING CONFIGURATION REGISTER | --- | FLAGS
1 | 0 | 1 | VSTRING1_START | Vdc | FLOAT
2 | 0 | 2 | VSTRING2_START | Vdc | FLOAT
3 | 0 | 3 | VSTRING1 UV | Vdc | FLOAT
4 | 0 | 4 | VSTRING1 OV | Vdc | FLOAT
5 | 0 | 5 | VSTRING2 UV | Vdc | FLOAT
6 | 0 | 6 | VSTRING2 OV | Vdc | FLOAT
7 | 0 | 7 | VSTRING_OK_TOUT | ms | UI32
8 | 0 | 8 | VSTRING_UV_TOUT CONNECTED | ms | UI32
9 | 0 | 9 | VSTRING_OV_TOUT | ms | UI32
10 | 0 | 10 | VSTRING UV ZERO POWER TOUT DISCONNECTED | ms | UI32
11 | 0 | 11 | POWER SAVING START THRESHOLD | W | FLOAT
12 | 0 | 12 | POWER SAVING THRESHOLD HYSTERESYS | % | FLOAT
32 | 0 | 32 | ISTRING OC SW | A | FLOAT
33 | 0 | 33 | ISTRING OC SW TOUT | ms | UI32
34 | 0 | 34 | VSTRING_NIGHT_MODE_THRESHOLD | Vdc | FLOAT
35 | 0 | 35 | VSTRING_NIGHT_MODE_TOUT | ms | UI32
36 | 0 | 36 | ISTRING_ZERO_POWER_THRESHOLD | A | FLOAT
37 | 0 | 37 | NEGATIVE STRING CURRENT SATURATION | A | FLOAT
38 | 0 | 38 | NEGATIVE STRING CURRENT THRESHOLD | A | FLOAT
39 | 0 | 39 | NEGATIVE STRING CURRENT TOUT | ms | UI32
40 | 0 | 40 | I2T_ENABLE_CURRENT_THRESHOLD | A | FLOAT
41 | 0 | 41 | I2T_KI | --- | FLOAT
42 | 0 | 42 | I2T_KD | --- | FLOAT
43 | 0 | 43 | I2T_COUNTER_THRESHOLD | --- | FLOAT
44 | 0 | 44 | POL INV ISTRING PERCENTILE THRESHOLD | --- | FLOAT
45 | 0 | 45 | POL INV ENTRANCE TIMEOUT | ms | UI32
46 | 0 | 46 | POL INV EXIT TIMEOUT | ms | UI32
256 | 1 | 0 | PV SCAN CONFIGURATION REGISTER | --- | FLAGS
257 | 1 | 1 | PV SCAN EXECUTION PERIOD | ms | UI32
258 | 1 | 2 | PV SCAN VSTRING MIN | Vdc | FLOAT
259 | 1 | 3 | PV SCAN VSTRING MAX | Vdc | FLOAT
260 | 1 | 4 | PV SCAN BULK SET-POINT | Vdc | FLOAT
512 | 2 | 0 | GRID PROTECTION VOLT CONFIGURATION REGISTER | --- | FLAGS
513 | 2 | 1 | GRID PROTECTION VOLT DISABLE REGISTER (Phase R) | --- | FLAGS
514 | 2 | 2 | GRID PROTECTION VOLT DISABLE REGISTER (Phase S) | --- | FLAGS
515 | 2 | 3 | GRID PROTECTION VOLT DISABLE REGISTER (Phase T) | --- | FLAGS
516 | 2 | 4 | GRID PROTECTION VOLT DISABLE REGISTER (RS) | --- | FLAGS
517 | 2 | 5 | GRID PROTECTION VOLT DISABLE REGISTER (ST) | --- | FLAGS
518 | 2 | 6 | GRID PROTECTION VOLT DISABLE REGISTER (TR) | --- | FLAGS
519 | 2 | 7 | GRID PHASE MODE CONFIGURATION REGISTER | --- | FLAGS
520 | 2 | 8 | VGRID_NOM | Vac | FLOAT
521 | 2 | 9 | GRID_OK_TOUT | ms | UI32
522 | 2 | 10 | GRID OK TOUT AFTER GRID FAULT | ms | UI32
523 | 2 | 11 | VGRID_OK_MAX | Vac | FLOAT
524 | 2 | 12 | VGRID_OK_MIN | Vac | FLOAT
525 | 2 | 13 | VGRID_OV1 | Vac | FLOAT
526 | 2 | 14 | VGRID_OV2 | Vac | FLOAT
527 | 2 | 15 | VGRID_OV3 | Vac | FLOAT
528 | 2 | 16 | VGRID_OV4 | Vac | FLOAT
529 | 2 | 17 | VGRID_OV5 | Vac | FLOAT
530 | 2 | 18 | VGRID_OV6 | Vac | FLOAT
531 | 2 | 19 | VGRID_OV7 | Vac | FLOAT
532 | 2 | 20 | VGRID_OV8 | Vac | FLOAT
541 | 2 | 29 | VGRID_UV_1 | Vac | FLOAT
542 | 2 | 30 | VGRID_UV_2 | Vac | FLOAT
543 | 2 | 31 | VGRID_UV_3 | Vac | FLOAT
544 | 2 | 32 | VGRID_UV_4 | Vac | FLOAT
545 | 2 | 33 | VGRID_UV_5 | Vac | FLOAT
546 | 2 | 34 | VGRID_UV_6 | Vac | FLOAT
547 | 2 | 35 | VGRID_UV_7 | Vac | FLOAT
548 | 2 | 36 | VGRID_UV_8 | Vac | FLOAT
557 | 2 | 45 | VGRID_OV_TOUT_1 | ms | UI32
558 | 2 | 46 | VGRID_OV_TOUT_2 | ms | UI32
559 | 2 | 47 | VGRID_OV_TOUT_3 | ms | UI32
560 | 2 | 48 | VGRID_OV_TOUT_4 | ms | UI32
561 | 2 | 49 | VGRID_OV_TOUT_5 | ms | UI32
562 | 2 | 50 | VGRID_OV_TOUT_6 | ms | UI32
563 | 2 | 51 | VGRID_OV_TOUT_7 | ms | UI32
564 | 2 | 52 | VGRID_OV_TOUT_8 | ms | UI32
573 | 2 | 61 | VGRID_UV_TOUT_1 | ms | UI32
574 | 2 | 62 | VGRID_UV_TOUT_2 | ms | UI32
575 | 2 | 63 | VGRID_UV_TOUT_3 | ms | UI32
576 | 2 | 64 | VGRID_UV_TOUT_4 | ms | UI32
577 | 2 | 65 | VGRID_UV_TOUT_5 | ms | UI32
578 | 2 | 66 | VGRID_UV_TOUT_6 | ms | UI32
579 | 2 | 67 | VGRID_UV_TOUT_7 | ms | UI32
580 | 2 | 68 | VGRID_UV_TOUT_8 | ms | UI32
589 | 2 | 77 | VAC PEAK O.V. | Vac | FLOAT
590 | 2 | 78 | VAC PEAK OV TOUT | ms | UI32
602 | 2 | 90 | GRID_OK_TOUT CONC. | ms | UI32
603 | 2 | 91 | GRID OK TOUT AFTER GRID FAULT CONC. | ms | UI32
604 | 2 | 92 | VGRID_OK_MAX CONC. | Vac | FLOAT
605 | 2 | 93 | VGRID_OK_MIN CONC. | Vac | FLOAT
606 | 2 | 94 | VGRID_OV CONC_1 | Vac | FLOAT
607 | 2 | 95 | VGRID_OV CONC_2 | Vac | FLOAT
608 | 2 | 96 | VGRID_OV CONC_3 | Vac | FLOAT
609 | 2 | 97 | VGRID_OV CONC_4 | Vac | FLOAT
610 | 2 | 98 | VGRID_OV CONC_5 | Vac | FLOAT
611 | 2 | 99 | VGRID_OV CONC_6 | Vac | FLOAT
612 | 2 | 100 | VGRID_OV CONC_7 | Vac | FLOAT
613 | 2 | 101 | VGRID_OV CONC_8 | Vac | FLOAT
622 | 2 | 110 | VGRID_UV CONC_1 | Vac | FLOAT
623 | 2 | 111 | VGRID_UV CONC_2 | Vac | FLOAT
624 | 2 | 112 | VGRID_UV CONC_3 | Vac | FLOAT
625 | 2 | 113 | VGRID_UV CONC_4 | Vac | FLOAT
626 | 2 | 114 | VGRID_UV CONC_5 | Vac | FLOAT
627 | 2 | 115 | VGRID_UV CONC_6 | Vac | FLOAT
628 | 2 | 116 | VGRID_UV CONC_7 | Vac | FLOAT
629 | 2 | 117 | VGRID_UV CONC_8 | Vac | FLOAT
638 | 2 | 126 | VGRID_OV_TOUT CONC_1 | ms | UI32
639 | 2 | 127 | VGRID_OV_TOUT CONC_2 | ms | UI32
640 | 2 | 128 | VGRID_OV_TOUT CONC_3 | ms | UI32
641 | 2 | 129 | VGRID_OV_TOUT CONC_4 | ms | UI32
642 | 2 | 130 | VGRID_OV_TOUT CONC_5 | ms | UI32
643 | 2 | 131 | VGRID_OV_TOUT CONC_6 | ms | UI32
644 | 2 | 132 | VGRID_OV_TOUT CONC_7 | ms | UI32
645 | 2 | 133 | VGRID_OV_TOUT CONC_8 | ms | UI32
654 | 2 | 142 | VGRID_UV_TOUT CONC_1 | ms | UI32
655 | 2 | 143 | VGRID_UV_TOUT CONC_2 | ms | UI32
656 | 2 | 144 | VGRID_UV_TOUT CONC_3 | ms | UI32
657 | 2 | 145 | VGRID_UV_TOUT CONC_4 | ms | UI32
658 | 2 | 146 | VGRID_UV_TOUT CONC_5 | ms | UI32
659 | 2 | 147 | VGRID_UV_TOUT CONC_6 | ms | UI32
660 | 2 | 148 | VGRID_UV_TOUT CONC_7 | ms | UI32
661 | 2 | 149 | VGRID_UV_TOUT CONC_8 | ms | UI32
677 | 2 | 165 | GRID PRESENCE THR | Vac | FLOAT
678 | 2 | 166 | MAX_VGRID_DUTY_LIMITATION | Vac | FLOAT
680 | 2 | 168 | MAX_AVG_VGRID_THRESHOLD | Vac | FLOAT
681 | 2 | 169 | MAX_AVG_VGRID_BLOCK_LENGTH | --- | UI32
682 | 2 | 170 | MAX_AVG_VGRID_BUFFER_LENGTH | --- | UI32
690 | 2 | 178 | MAX_AVG_VGRID_REG_CONFIG_REG | --- | FLAGS
691 | 2 | 179 | MAX_AVG_VGRID_REG_THR_ENABLE | Vac | FLOAT
692 | 2 | 180 | MAX_AVG_VGRID_REG_THR_DISABLE | Vac | FLOAT
693 | 2 | 181 | MAX_AVG_VGRID_REG_REFERENCE | Vac | FLOAT
694 | 2 | 182 | MAX_AVG_VGRID_REG_KI | --- | FLOAT
695 | 2 | 183 | MAX_AVG_VGRID_REG_SLOPE_NORMAL_POS | % | FLOAT
696 | 2 | 184 | MAX_AVG_VGRID_REG_SLOPE_NORMAL_NEG | % | FLOAT
697 | 2 | 185 | MAX_AVG_VGRID_REG_SLOPE_RED_POS | % | FLOAT
698 | 2 | 186 | MAX_AVG_VGRID_REG_SLOPE_RED_NEG | % | FLOAT
699 | 2 | 187 | MAX_AVG_VGRID_REG_SLOPE_RED_ENABLE_THR | % | FLOAT
700 | 2 | 188 | MAX_AVG_VGRID_REG_AVG_RESET_TIMEOUT | ms | UI32
768 | 3 | 0 | GRID PROTECTION FREQ CONFIGURATION REGISTER | --- | FLAGS
769 | 3 | 1 | GRID PROTECTION FREQ DISABLE REGISTER (Phase R) | --- | FLAGS
770 | 3 | 2 | GRID PROTECTION FREQ DISABLE REGISTER (Phase S) | --- | FLAGS
771 | 3 | 3 | GRID PROTECTION FREQ DISABLE REGISTER (Phase T) | --- | FLAGS
772 | 3 | 4 | FGRID_NOM | Hz | FLOAT
773 | 3 | 5 | FGRID_OK_MAX | Hz | FLOAT
774 | 3 | 6 | FGRID_OK_MIN | Hz | FLOAT
775 | 3 | 7 | FGRID_OF_1 | Hz | FLOAT
776 | 3 | 8 | FGRID_OF_2 | Hz | FLOAT
777 | 3 | 9 | FGRID_OF_3 | Hz | FLOAT
778 | 3 | 10 | FGRID_OF_4 | Hz | FLOAT
779 | 3 | 11 | FGRID_OF_5 | Hz | FLOAT
780 | 3 | 12 | FGRID_OF_6 | Hz | FLOAT
781 | 3 | 13 | FGRID_OF_7 | Hz | FLOAT
782 | 3 | 14 | FGRID_OF_8 | Hz | FLOAT
791 | 3 | 23 | FGRID_UF_1 | Hz | FLOAT
792 | 3 | 24 | FGRID_UF_2 | Hz | FLOAT
793 | 3 | 25 | FGRID_UF_3 | Hz | FLOAT
794 | 3 | 26 | FGRID_UF_4 | Hz | FLOAT
795 | 3 | 27 | FGRID_UF_5 | Hz | FLOAT
796 | 3 | 28 | FGRID_UF_6 | Hz | FLOAT
797 | 3 | 29 | FGRID_UF_7 | Hz | FLOAT
798 | 3 | 30 | FGRID_UF_8 | Hz | FLOAT
807 | 3 | 39 | FGRID_OF_TOUT_1 | ms | UI32
808 | 3 | 40 | FGRID_OF_TOUT_2 | ms | UI32
809 | 3 | 41 | FGRID_OF_TOUT_3 | ms | UI32
810 | 3 | 42 | FGRID_OF_TOUT_4 | ms | UI32
811 | 3 | 43 | FGRID_OF_TOUT_5 | ms | UI32
812 | 3 | 44 | FGRID_OF_TOUT_6 | ms | UI32
813 | 3 | 45 | FGRID_OF_TOUT_7 | ms | UI32
814 | 3 | 46 | FGRID_OF_TOUT_8 | ms | UI32
823 | 3 | 55 | FGRID_UF_TOUT_1 | ms | UI32
824 | 3 | 56 | FGRID_UF_TOUT_2 | ms | UI32
825 | 3 | 57 | FGRID_UF_TOUT_3 | ms | UI32
826 | 3 | 58 | FGRID_UF_TOUT_4 | ms | UI32
827 | 3 | 59 | FGRID_UF_TOUT_5 | ms | UI32
828 | 3 | 60 | FGRID_UF_TOUT_6 | ms | UI32
829 | 3 | 61 | FGRID_UF_TOUT_7 | ms | UI32
830 | 3 | 62 | FGRID_UF_TOUT_8 | ms | UI32
838 | 3 | 70 | VGRID_FOR_FGRID_DIS | Vac | FLOAT
839 | 3 | 71 | FGRID BUFFER SIZE | --- | UI32
1024 | 4 | 0 | DC INJ PROT DIS REG | --- | FLAGS
1025 | 4 | 1 | DC INJ MAX 1 | A | FLOAT
1026 | 4 | 2 | DC INJ MAX 2 | A | FLOAT
1027 | 4 | 3 | DC INJ BUFFER SIZE1 | --- | UI32
1028 | 4 | 4 | DC INJ BUFFER SIZE2 | --- | UI32
1029 | 4 | 5 | DC INJ MAX 1 AS % OF IAC NOM | %/A | FLOAT
1030 | 4 | 6 | DC INJ MAX 2 AS % OF IAC NOM | %/A | FLOAT
1031 | 4 | 7 | DC INJ MAX 1 OFFSET | A | FLOAT
1032 | 4 | 8 | DC INJ MAX 2 OFFSET | A | FLOAT
1280 | 5 | 0 | DERATING OVER FREQ CONFIGURATION REGISTER | --- | FLAGS
1281 | 5 | 1 | O.F DERATING STOP FREQ | Hz | FLOAT
1282 | 5 | 2 | U.F DERATING STOP FREQ | Hz | FLOAT
1283 | 5 | 3 | O.F DERATING START FREQ | Hz | FLOAT
1284 | 5 | 4 | U.F DERATING START FREQ | Hz | FLOAT
1285 | 5 | 5 | FGRID DERATING OK MAX | Hz | FLOAT
1286 | 5 | 6 | FGRID DERATING OK MIN | Hz | FLOAT
1287 | 5 | 7 | FGRID O.F. RESET TOUT | ms | UI32
1288 | 5 | 8 | FGRID U.F. RESET TOUT | ms | UI32
1289 | 5 | 9 | RESTORE RAMP SLOPE | %/min | FLOAT
1290 | 5 | 10 | MIN RESTORE RAMP SLOPE | %/min | FLOAT
1291 | 5 | 11 | FGRID DERATIN MIN POWER | W | FLOAT
1292 | 5 | 12 | FGRID O.F TURN ON DELAY | ms | UI32
1293 | 5 | 13 | FGRID U.F TURN ON DELAY | ms | UI32
1294 | 5 | 14 | O.F DERATING STOP POWER | %Pn | FLOAT
1295 | 5 | 15 | U.F DERATING STOP POWER | %Pn | FLOAT
1536 | 6 | 0 | ANTI ISLANDING CONFIGURATION REGISTER | --- | FLAGS
1537 | 6 | 1 | ANTI ISLANDING REPETITION TIME | ms | UI32
1538 | 6 | 2 | ANTI ISLANDING DELTA FREQ THRESHOLD | Hz | FLOAT
1539 | 6 | 3 | ANTI ISLANDING FULL POWER PERCENT | --- | FLOAT
1540 | 6 | 4 | ANTI ISLANDING LOW POWER PERCENT | --- | FLOAT
1541 | 6 | 5 | ANTI ISLANDING MIN PULSE REACTIVE POWER | W | FLOAT
1542 | 6 | 6 | ANTI ISLANDING MIN ACTIVE POWER | W | FLOAT
1543 | 6 | 7 | ANTI ISLANDING GRID PROTECTIONS REDUCED TIME | ms | UI32
1546 | 6 | 10 | ANTI ISLANDING RAMP UP FOR REACTIVE CURRENT | --- | FLOAT
1547 | 6 | 11 | ANTI ISLANDING CURRENT FRACTION | --- | FLOAT
1566 | 6 | 30 | PASSIVE ANTI ISLANDING CONFIGURATION REGISTER | --- | FLAGS
1567 | 6 | 31 | PASSIVE ANTI ISLANDING BUFFER LENGTH | --- | UI32
1568 | 6 | 32 | PASSIVE ANTI ISLANDING DELTA FREQ THRESHOLD | Hz | FLOAT
1569 | 6 | 33 | PASSIVE ANTI ISLANDING REDUCED POWER TIMEOUT | ms | UI32
1570 | 6 | 34 | PASSIVE ANTI ISLANDING MIN ACTIVE POWER | W | FLOAT
1586 | 6 | 50 | ACTIVE FREQUENCY SHIFT CONFIGURATION REGISTER | --- | FLAGS
1587 | 6 | 51 | ACTIVE FREQUENCY SHIFT GAIN | --- | FLOAT
1600 | 6 | 64 | ACTIVE FREQUENCY DRIFT CONFIGURATION REGISTER | --- | FLAGS
1601 | 6 | 65 | ACTIVE FREQUENCY DRIFT Tdrift Min | msec | UI32
1602 | 6 | 66 | ACTIVE FREQUENCY DRIFT FIRST LEVEL THRESHOLD | Hz | FLOAT
1603 | 6 | 67 | ACTIVE FREQUENCY DRIFT SECOND LEVEL THRESHOLD | Hz | FLOAT
1604 | 6 | 68 | AFD FIRST LEVEL N CONSECUTIVE TIMES THRESHOLD | --- | UI32
1605 | 6 | 69 | AFD FIXED PERTURBATION | Hz | FLOAT
1606 | 6 | 70 | AFD FIRST LEVEL KP | --- | FLOAT
1607 | 6 | 71 | AFD SECOND LEVEL KP | --- | FLOAT
1608 | 6 | 72 | AFD POSITIVE DELTA F PERTURBATION CONSECUTIVE CYCLES | --- | UI32
1609 | 6 | 73 | AFD NEGATIVE DELTA F PERTURBATION CONSECUTIVE CYCLES | --- | UI32
1610 | 6 | 74 | AFD ISLAND DETECTION DELTA FREQ THRESHOLD | Hz | FLOAT
1792 | 7 | 0 | BULK CONFIGURATION REGISTER | --- | FLAGS
1793 | 7 | 1 | BULK PROTECTION DISABLE REGISTER | --- | FLAGS
1794 | 7 | 2 | MIN MAX ATTENUATION FACTOR | --- | FLOAT
1795 | 7 | 3 | VBULK OV | V | FLOAT
1796 | 7 | 4 | VBULK UV | V | FLOAT
1797 | 7 | 5 | VBULK OV TOUT | ms | UI32
1798 | 7 | 6 | VBULK UV TOUT | ms | UI32
1799 | 7 | 7 | VBULK OV MID | V | FLOAT
1800 | 7 | 8 | VBULK UV MID | V | FLOAT
1801 | 7 | 9 | VBULK OV ABSOLUTE | V | FLOAT
1802 | 7 | 10 | VBULK OV MID TOUT | ms | UI32
1803 | 7 | 11 | VBULK UV MID TOUT | ms | UI32
1804 | 7 | 12 | MAX VBULK SET-POINT | V | FLOAT
1805 | 7 | 13 | VBULK MID OUT OF RANGE LOW | V | FLOAT
1806 | 7 | 14 | VBULK MID OUT OF RANGE HIGH | V | FLOAT
1807 | 7 | 15 | VBULK MID OUT OF RANGE TOUT | ms | UI32
1808 | 7 | 16 | VBULK MID OV ABS | V | FLOAT
1809 | 7 | 17 | DELTA BULK | V | FLOAT
1810 | 7 | 18 | DELTA BULK TOUT | ms | UI32
1822 | 7 | 30 | BYPASS DISABLE TOUT DUE TO HIGH INPUT CURRENT | ms | UI32
1823 | 7 | 31 | BYPASS ENABLE TOUT AFTER DISABLE DUE TO HIGH INPUT CURRENT | ms | UI32
1824 | 7 | 32 | BYPASS DISABLE TOUT DUE TO HIGH INPUT POWER | ms | UI32
1825 | 7 | 33 | BYPASS ENABLE TOUT AFTER DISABLE DUE TO HIGH INPUT POWER | ms | UI32
1826 | 7 | 34 | BYPASS DISABLE TOUT DUE TO INPUT CURRENT UMBALANCE | ms | UI32
1827 | 7 | 35 | BYPASS ENABLE TOUT AFTER DISABLE DUE TO INPUT CURRENT UMBALANCE | ms | UI32
1832 | 7 | 40 | K FOR BULK SET-POINT RESPECT TO GRID VOLTAGE | --- | FLOAT
1833 | 7 | 41 | Q FOR BULK SET-POINT RESPECT TO GRID VOLTAGE | V | FLOAT
1834 | 7 | 42 | BULK SOFT-START SLOPE | V/s | FLOAT
1835 | 7 | 43 | BULK SOFT-START TOUT | ms | UI32
1842 | 7 | 50 | BULK FROM GRID POWER THRESHOLD | W | FLOAT
1843 | 7 | 51 | BULK FROM GRID TOUT | ms | UI32
1844 | 7 | 52 | BULK PRECHARGE SET POINT | V | FLOAT
1845 | 7 | 53 | BULK STAND ALONE SET POINT | V | FLOAT
2048 | 8 | 0 | MPPT CONFIGURATION REGISTER | --- | FLAGS
2049 | 8 | 1 | MPPT FREQ | Hz | FLOAT
2050 | 8 | 2 | MPPT AMPLITUDE | Vdc | FLOAT
2051 | 8 | 3 | MPPT KI | Vdc | FLOAT
2052 | 8 | 4 | MPPT KP | Vdc | FLOAT
2053 | 8 | 5 | SET POINT 1 | Vdc | FLOAT
2054 | 8 | 6 | SET POINT 2 | Vdc | FLOAT
2059 | 8 | 11 | WAITING TIME FOR MPPT ALGORITHM | Vdc | UI32
2060 | 8 | 12 | DELTA BULK STEP FOR MPPT | Vdc | FLOAT
2061 | 8 | 13 | DELTA BULK STEP FOR SWAP | Vdc | FLOAT
2062 | 8 | 14 | TIME FOR VARIATION DURING SWAP PHASE | Vdc | UI32
2063 | 8 | 15 | MPPT SLAVE POWER START | W | FLOAT
2064 | 8 | 16 | PRE-MPPT VOLTAGE (% of Voc at startup) | % | FLOAT
2065 | 8 | 17 | MPPT POWER INTEGRATION TIME | ms | UI32
2304 | 9 | 0 | RAMP AFTER CONNECTION CONFIGURATION REGISTER | --- | FLAGS
2305 | 9 | 1 | RAMP SLOPE NORMAL | %/min | FLOAT
2306 | 9 | 2 | RAMP SLOPE FAULT | %/min | FLOAT
2307 | 9 | 3 | RAMP MIN POWER | W | FLOAT
2308 | 9 | 4 | RAMP START DELAY | ms | UI32
2324 | 9 | 20 | NORMAL RAMP UP CONFIGURATION REGISTER | --- | FLAGS
2325 | 9 | 21 | NORMAL RAMP UP SLOPE RISING | %/min | FLOAT
2326 | 9 | 22 | NORMAL RAMP UP SLOPE FALLING | %/min | FLOAT
2327 | 9 | 23 | NORMAL RAMP UP OFFSET | W | FLOAT
2560 | 10 | 0 | G.I. RELAY CLOSURE TIME | ms | UI32
2562 | 10 | 2 | WIND FREQ BUFFER SIZE | --- | UI32
2563 | 10 | 3 | COIL RATIO N1/N2 | --- | FLOAT
2816 | 11 | 0 | AUTOTEST ENEL CONFIGURATION REGISTER | --- | FLAGS
2817 | 11 | 1 | AUTOTEST ENEL TOUT | ms | UI32
2818 | 11 | 2 | AUTOTEST ENEL V RAMP SLOPE | --- | FLOAT
2819 | 11 | 3 | AUTOTEST ENEL F RAMP SLOPE | --- | FLOAT
3072 | 12 | 0 | RIDE THROUGH CONFIG REG | --- | FLAGS
3073 | 12 | 1 | RIDE THROUGH DISABLE REG | --- | FLAGS
3074 | 12 | 2 | HVRT - VAC PERCENT INPUT THRESHOLD | % | FLOAT
3075 | 12 | 3 | HVRT - VAC PERCENT OUTPUT THRESHOLD | % | FLOAT
3076 | 12 | 4 | SYM - K LOW VOLTAGE RIDE THROUGH | --- | FLOAT
3077 | 12 | 5 | LVRT - ACTIVE CURRENT INJECTION DURING LVRT | A | FLOAT
3078 | 12 | 6 | LVRT - VAC PERCENT INPUT THRESHOLD | % | FLOAT
3079 | 12 | 7 | LVRT - VAC PERCENT OUTPUT THRESHOLD | % | FLOAT
3080 | 12 | 8 | MAXIMUM REACTIVE CURRENT | A | FLOAT
3081 | 12 | 9 | SYM - POST MANTEINANCE TIME | ms | UI32
3082 | 12 | 10 | RECESSIVE SEQUENCE PEAK VOLTAGE DETECT | Vac | FLOAT
3083 | 12 | 11 | DOMINANT SEQUENCE CURRENT PI KP COEFFICIENT | --- | FLOAT
3084 | 12 | 12 | DOMINANT SEQUENCE CURRENT PI KI COEFFICIENT | --- | FLOAT
3085 | 12 | 13 | KP DELTABULK GAIN | --- | FLOAT
3086 | 12 | 14 | LVRT - VAC DELTA OUTPUT THRESHOLD | Vac | FLOAT
3087 | 12 | 15 | LVRT - DELTA BULK THRESHOLD | Vac | FLOAT
3088 | 12 | 16 | SYM - REDUCTION CURRENT FRACTION | --- | FLOAT
3089 | 12 | 17 | SYM - RECOGNITION TIME | ms | FLOAT
3090 | 12 | 18 | SYM LVRT - REDUCTION CURRENT V PEAK THRESHOLD | Vac | FLOAT
3091 | 12 | 19 | ASYM - PEAK NEGATIVE SEQUENCY THRESHOLD | V | FLOAT
3092 | 12 | 20 | ASYM - K LOW VOLTAGE RIDE TROUGHT | --- | FLOAT
3093 | 12 | 21 | ASYM - POST MANTEINANCE TIME | ms | UI32
3094 | 12 | 22 | ASYM - REDUCTION CURRENT FRACTION | --- | FLOAT
3095 | 12 | 23 | ASYM - RECOGNITION TIME LVRT | ms | FLOAT
3096 | 12 | 24 | GATE BLOCK CONFIGURATION REGISTER | --- | FLAGS
3097 | 12 | 25 | GATE BLOCK LOW VOLTAGE THRESHOLD | Vac | FLOAT
3098 | 12 | 26 | GATEBLOCK HIGH VOLTAGE THRESHOLD | Vac | FLOAT
3099 | 12 | 27 | GATE BLOCK DELTAV THRESHOLD | V | FLOAT
3100 | 12 | 28 | GATE BLOCK CURRENT ERROR THRESHOLD | A | FLOAT
3101 | 12 | 29 | GATE BLOCK dv/dt THRESHOLD | V/s | FLOAT
3102 | 12 | 30 | GATE BLOCK NEG PEAK HIGH THRESHOLD | V | FLOAT
3103 | 12 | 31 | GATE BLOCK TIME BEFORE FAULT RIDE THROUGH | ms | UI32
3104 | 12 | 32 | GATE BLOCK TIME AFTER FAULT RIDE THROUGH | ms | UI32
3105 | 12 | 33 | SYM HVRT - REDUCTION CURRENT V PEAK THRESHOLD | Vac | FLOAT
3112 | 12 | 40 | FAULT RIDE THROUGH CONFIGURATION REGISTER | --- | FLAGS
3113 | 12 | 41 | DERATING PERCENTUAL | %/W | FLOAT
3114 | 12 | 42 | HVRT TH ZERO POWER ON | Vac | FLOAT
3115 | 12 | 43 | HVRT TH ZERO POWER OFF | Vac | FLOAT
3116 | 12 | 44 | LVRT TH ZERO POWER ON | Vac | FLOAT
3117 | 12 | 45 | LVRT TH ZERO POWER OFF | Vac | FLOAT
3118 | 12 | 46 | HFRT TH ZERO POWER ON | Hz | FLOAT
3119 | 12 | 47 | HFRT TH ZERO POWER OFF | Hz | FLOAT
3120 | 12 | 48 | LFRT TH ZERO POWER ON | Hz | FLOAT
3121 | 12 | 49 | LFRT TH ZERO POWER OFF | Hz | FLOAT
3328 | 13 | 0 | ISOLATION CHECKS DISABLE REGISTER | --- | FLAGS
3329 | 13 | 1 | GROUNDING MODE | --- | UI32
3330 | 13 | 2 | MIN R-ISO | Ohm | FLOAT
3331 | 13 | 3 | DELAY BETWEEN Vgnd SAMPLES FOR R-ISO CHECK | ms | UI32
3332 | 13 | 4 | MAX V_GROUND 1 | Vdc | FLOAT
3333 | 13 | 5 | MAX V_GROUND 2 | Vdc | FLOAT
3334 | 13 | 6 | MAX V_GROUND 1 TOUT | ms | UI32
3335 | 13 | 7 | MAX V_GROUND 2 TOUT | ms | UI32
3336 | 13 | 8 | DELAY AFTER RELAY SETTING | ms | UI32
3337 | 13 | 9 | MAX VOLTAGE PERCENTILE DIFFERENCE | % | FLOAT
3338 | 13 | 10 | MAX RISO PERCENTILE DIFFERENCE | % | FLOAT
3339 | 13 | 11 | DELAY FOR R-ISO CHECK REPETITION AFTER R-ISO LOW EVENT | ms | UI32
3584 | 14 | 0 | LEAKAGE CHECKS DISABLE REGISTER | --- | FLAGS
3585 | 14 | 1 | LEAKAGE RMS ABSOLUTE TH | A | FLOAT
3586 | 14 | 2 | LEAKAGE RMS DYNAMIC HIGH TH | A | FLOAT
3587 | 14 | 3 | LEAKAGE RMS DYNAMIC MEDIUM TH | A | FLOAT
3588 | 14 | 4 | LEAKAGE RMS DYNAMIC LOW TH | A | FLOAT
3589 | 14 | 5 | LEAKAGE RESISTIVE ABSOLUTE TH | A | FLOAT
3590 | 14 | 6 | LEAKAGE RESISTIVE DYNAMIC HIGH TH | A | FLOAT
3591 | 14 | 7 | LEAKAGE RESISTIVE DYNAMIC MEDIUM TH | A | FLOAT
3592 | 14 | 8 | LEAKAGE RESISTIVE DYNAMIC LOW TH | A | FLOAT
3593 | 14 | 9 | LEAKAGE RMS ABSOLUTE TIMEOUT | ms | UI32
3594 | 14 | 10 | LEAKAGE RMS DYNAMIC HIGH TIMEOUT | ms | UI32
3595 | 14 | 11 | LEAKAGE RMS DYNAMIC MEDIUM TIMEOUT | ms | UI32
3596 | 14 | 12 | LEAKAGE RMS DYNAMIC LOW TIMEOUT | ms | UI32
3597 | 14 | 13 | LEAKAGE RESISTIVE ABSOLUTE TIMEOUT | ms | UI32
3598 | 14 | 14 | LEAKAGE RESISTIVE DYNAMIC HIGH TIMEOUT | ms | UI32
3599 | 14 | 15 | LEAKAGE RESISTIVE DYNAMIC MEDIUM TIMEOUT | ms | UI32
3600 | 14 | 16 | LEAKAGE RESISTIVE DYNAMIC LOW TIMEOUT | ms | UI32
3840 | 15 | 0 | COUNTRY SELECTION CONFIGURATION REGISTER | --- | UI32
3841 | 15 | 1 | GRID STD CODE | --- | UI32
3842 | 15 | 2 | MODEL CODE | --- | UI32
3843 | 15 | 3 | INPUT MODE | --- | UI32
3844 | 15 | 4 | IAC NOMINAL | Arms | FLOAT
3845 | 15 | 5 | PAC NOMINAL | W | FLOAT
3846 | 15 | 6 | MAX IAC ACTIVE | Arms | FLOAT
3847 | 15 | 7 | MAX IAC REACT | A | FLOAT
3848 | 15 | 8 | MAX IAC APPAR | A | FLOAT
3849 | 15 | 9 | MAX PAC ACTIVE | W | FLOAT
3850 | 15 | 10 | MAX QAC REACT | VAR | FLOAT
3851 | 15 | 11 | MAX SAC APPAR | VA | FLOAT
3852 | 15 | 12 | MAX IGRID OC | Arms | FLOAT
3853 | 15 | 13 | PIN MAX | W | FLOAT
3854 | 15 | 14 | I IN MAX | A | FLOAT
3855 | 15 | 15 | I IN MAX OC | A | FLOAT
3856 | 15 | 16 | MAX Qmax/Smax POSITIVE LIMIT FOR GRID STD | --- | FLOAT
3857 | 15 | 17 | MIN Qmax/Smax NEGATIVE LIMIT FOR GRID STD | --- | FLOAT
3858 | 15 | 18 | MAX ABSOLUTE PAC ACTIVE | W | FLOAT
3859 | 15 | 19 | Pmax (par. 521) RESPECT TO Pmax_absolute (par. 530) GAIN | % | FLOAT
3860 | 15 | 20 | Pmax (par. 521) RESPECT TO Pmax_absolute (par. 530) OFFSET | W | FLOAT
3861 | 15 | 21 | MAX NEGATIVE PAC ACTIVE | W | FLOAT
3862 | 15 | 22 | Total installed AE power of the plant | W | FLOAT
3863 | 15 | 23 | CONTROL MODE | --- | FLAGS
3864 | 15 | 24 | MAX IGRID OC TOUT | ms | UI32
3865 | 15 | 25 | IGRID UNBALANCE | Arms | FLOAT
3866 | 15 | 26 | IGRID UNBALANCE TOUT | ms | UI32
3867 | 15 | 27 | PAC CHARGE NOM | W | FLOAT
4096 | 16 | 0 | Vcharge Max | Vdc | FLOAT
4097 | 16 | 1 | Icharge Max | Vdc | FLOAT
4098 | 16 | 2 | Vdischarge Min | Vdc | FLOAT
4099 | 16 | 3 | I Discharge Max | Vdc | FLOAT
4100 | 16 | 4 | Pcharge Max | Vdc | FLOAT
4101 | 16 | 5 | Pdischarge Max | Vdc | FLOAT
4102 | 16 | 6 | Charge Bulk Ok | Vdc | FLOAT
4103 | 16 | 7 | Charge Bulk Nok | Vdc | FLOAT
4104 | 16 | 8 | Charge Bulk Ok TOUT | Vdc | UI32
4105 | 16 | 9 | Charge Bulk Nok TOUT | Vdc | UI32
4106 | 16 | 10 | Disch Vbatt OK | Vdc | FLOAT
4107 | 16 | 11 | Disch Vbatt Nok | Vdc | FLOAT
4108 | 16 | 12 | Disch Vbatt Ok TOUT | Vdc | UI32
4109 | 16 | 13 | Disch Vbatt Nok TOUT | Vdc | UI32
4110 | 16 | 14 | Vbatt OV | Vdc | FLOAT
4111 | 16 | 15 | Vbatt OV TOUT | ms | UI32
4352 | 17 | 0 | DERATING DISABLE REGISTER | --- | FLAGS
4353 | 17 | 1 | DERATING CONTROL 0 - Input measure ID | --- | FLAGS
4354 | 17 | 2 | DERATING CONTROL 0 - Control parameter ID | --- | FLAGS
4355 | 17 | 3 | DERATING CONTROL 0 - Input measure START | --- | FLOAT
4356 | 17 | 4 | DERATING CONTROL 0 - Input measure STOP | --- | FLOAT
4357 | 17 | 5 | DERATING CONTROL 0 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4358 | 17 | 6 | DERATING CONTROL 0 - CONFIGURATION REGISTER | --- | FLAGS
4359 | 17 | 7 | DERATING CONTROL 0 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4360 | 17 | 8 | DERATING CONTROL 1 - Input measure ID | --- | FLAGS
4361 | 17 | 9 | DERATING CONTROL 1 - Control parameter ID | --- | FLAGS
4362 | 17 | 10 | DERATING CONTROL 1 - Input measure START | --- | FLOAT
4363 | 17 | 11 | DERATING CONTROL 1 - Input measure STOP | --- | FLOAT
4364 | 17 | 12 | DERATING CONTROL 1 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4365 | 17 | 13 | DERATING CONTROL 1 - CONFIGURATION REGISTER | --- | FLAGS
4366 | 17 | 14 | DERATING CONTROL 1 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4367 | 17 | 15 | DERATING CONTROL 2 - Input measure ID | --- | FLAGS
4368 | 17 | 16 | DERATING CONTROL 2 - Control parameter ID | --- | FLAGS
4369 | 17 | 17 | DERATING CONTROL 2 - Input measure START | --- | FLOAT
4370 | 17 | 18 | DERATING CONTROL 2 - Input measure STOP | --- | FLOAT
4371 | 17 | 19 | DERATING CONTROL 2 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4372 | 17 | 20 | DERATING CONTROL 2 - CONFIGURATION REGISTER | --- | FLAGS
4373 | 17 | 21 | DERATING CONTROL 2 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4374 | 17 | 22 | DERATING CONTROL 3 - Input measure ID | --- | FLAGS
4375 | 17 | 23 | DERATING CONTROL 3 - Control parameter ID | --- | FLAGS
4376 | 17 | 24 | DERATING CONTROL 3 - Input measure START | --- | FLOAT
4377 | 17 | 25 | DERATING CONTROL 3 - Input measure STOP | --- | FLOAT
4378 | 17 | 26 | DERATING CONTROL 3 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4379 | 17 | 27 | DERATING CONTROL 3 - CONFIGURATION REGISTER | --- | FLAGS
4380 | 17 | 28 | DERATING CONTROL 3 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4381 | 17 | 29 | DERATING CONTROL 4 - Input measure ID | --- | FLAGS
4382 | 17 | 30 | DERATING CONTROL 4 - Control parameter ID | --- | FLAGS
4383 | 17 | 31 | DERATING CONTROL 4 - Input measure START | --- | FLOAT
4384 | 17 | 32 | DERATING CONTROL 4 - Input measure STOP | --- | FLOAT
4385 | 17 | 33 | DERATING CONTROL 4 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4386 | 17 | 34 | DERATING CONTROL 4 - CONFIGURATION REGISTER | --- | FLAGS
4387 | 17 | 35 | DERATING CONTROL 4 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4388 | 17 | 36 | DERATING CONTROL 5 - Input measure ID | --- | FLAGS
4389 | 17 | 37 | DERATING CONTROL 5 - Control parameter ID | --- | FLAGS
4390 | 17 | 38 | DERATING CONTROL 5 - Input measure START | --- | FLOAT
4391 | 17 | 39 | DERATING CONTROL 5 - Input measure STOP | --- | FLOAT
4392 | 17 | 40 | DERATING CONTROL 5 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4393 | 17 | 41 | DERATING CONTROL 5 - CONFIGURATION REGISTER | --- | FLAGS
4394 | 17 | 42 | DERATING CONTROL 5 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4395 | 17 | 43 | DERATING CONTROL 6 - Input measure ID | --- | FLAGS
4396 | 17 | 44 | DERATING CONTROL 6 - Control parameter ID | --- | FLAGS
4397 | 17 | 45 | DERATING CONTROL 6 - Input measure START | --- | FLOAT
4398 | 17 | 46 | DERATING CONTROL 6 - Input measure STOP | --- | FLOAT
4399 | 17 | 47 | DERATING CONTROL 6 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4400 | 17 | 48 | DERATING CONTROL 6 - CONFIGURATION REGISTER | --- | FLAGS
4401 | 17 | 49 | DERATING CONTROL 6 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4402 | 17 | 50 | DERATING CONTROL 7 - Input measure ID | --- | FLAGS
4403 | 17 | 51 | DERATING CONTROL 7 - Control parameter ID | --- | FLAGS
4404 | 17 | 52 | DERATING CONTROL 7 - Input measure START | --- | FLOAT
4405 | 17 | 53 | DERATING CONTROL 7 - Input measure STOP | --- | FLOAT
4406 | 17 | 54 | DERATING CONTROL 7 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4407 | 17 | 55 | DERATING CONTROL 7 - CONFIGURATION REGISTER | --- | FLAGS
4408 | 17 | 56 | DERATING CONTROL 7 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4409 | 17 | 57 | DERATING CONTROL 8 - Input measure ID | --- | FLAGS
4410 | 17 | 58 | DERATING CONTROL 8 - Control parameter ID | --- | FLAGS
4411 | 17 | 59 | DERATING CONTROL 8 - Input measure START | --- | FLOAT
4412 | 17 | 60 | DERATING CONTROL 8 - Input measure STOP | --- | FLOAT
4413 | 17 | 61 | DERATING CONTROL 8 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4414 | 17 | 62 | DERATING CONTROL 8 - CONFIGURATION REGISTER | --- | FLAGS
4415 | 17 | 63 | DERATING CONTROL 8 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4416 | 17 | 64 | DERATING CONTROL 9 - Input measure ID | --- | FLAGS
4417 | 17 | 65 | DERATING CONTROL 9 - Control parameter ID | --- | FLAGS
4418 | 17 | 66 | DERATING CONTROL 9 - Input measure START | --- | FLOAT
4419 | 17 | 67 | DERATING CONTROL 9 - Input measure STOP | --- | FLOAT
4420 | 17 | 68 | DERATING CONTROL 9 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4421 | 17 | 69 | DERATING CONTROL 9 - CONFIGURATION REGISTER | --- | FLAGS
4422 | 17 | 70 | DERATING CONTROL 9 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4423 | 17 | 71 | DERATING CONTROL 10 - Input measure ID | --- | FLAGS
4424 | 17 | 72 | DERATING CONTROL 10 - Control parameter ID | --- | FLAGS
4425 | 17 | 73 | DERATING CONTROL 10 - Input measure START | --- | FLOAT
4426 | 17 | 74 | DERATING CONTROL 10 - Input measure STOP | --- | FLOAT
4427 | 17 | 75 | DERATING CONTROL 10 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4428 | 17 | 76 | DERATING CONTROL 10 - CONFIGURATION REGISTER | --- | FLAGS
4429 | 17 | 77 | DERATING CONTROL 10 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4430 | 17 | 78 | DERATING CONTROL 11 - Input measure ID | --- | FLAGS
4431 | 17 | 79 | DERATING CONTROL 11 - Control parameter ID | --- | FLAGS
4432 | 17 | 80 | DERATING CONTROL 11 - Input measure START | --- | FLOAT
4433 | 17 | 81 | DERATING CONTROL 11 - Input measure STOP | --- | FLOAT
4434 | 17 | 82 | DERATING CONTROL 11 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4435 | 17 | 83 | DERATING CONTROL 11 - CONFIGURATION REGISTER | --- | FLAGS
4436 | 17 | 84 | DERATING CONTROL 11 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4437 | 17 | 85 | DERATING CONTROL 12 - Input measure ID | --- | FLAGS
4438 | 17 | 86 | DERATING CONTROL 12 - Control parameter ID | --- | FLAGS
4439 | 17 | 87 | DERATING CONTROL 12 - Input measure START | --- | FLOAT
4440 | 17 | 88 | DERATING CONTROL 12 - Input measure STOP | --- | FLOAT
4441 | 17 | 89 | DERATING CONTROL 12 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4442 | 17 | 90 | DERATING CONTROL 12 - CONFIGURATION REGISTER | --- | FLAGS
4443 | 17 | 91 | DERATING CONTROL 12 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4444 | 17 | 92 | DERATING CONTROL 13 - Input measure ID | --- | FLAGS
4445 | 17 | 93 | DERATING CONTROL 13 - Control parameter ID | --- | FLAGS
4446 | 17 | 94 | DERATING CONTROL 13 - Input measure START | --- | FLOAT
4447 | 17 | 95 | DERATING CONTROL 13 - Input measure STOP | --- | FLOAT
4448 | 17 | 96 | DERATING CONTROL 13 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4449 | 17 | 97 | DERATING CONTROL 13 - CONFIGURATION REGISTER | --- | FLAGS
4450 | 17 | 98 | DERATING CONTROL 13 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4451 | 17 | 99 | DERATING CONTROL 14 - Input measure ID | --- | FLAGS
4452 | 17 | 100 | DERATING CONTROL 14 - Control parameter ID | --- | FLAGS
4453 | 17 | 101 | DERATING CONTROL 14 - Input measure START | --- | FLOAT
4454 | 17 | 102 | DERATING CONTROL 14 - Input measure STOP | --- | FLOAT
4455 | 17 | 103 | DERATING CONTROL 14 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4456 | 17 | 104 | DERATING CONTROL 14 - CONFIGURATION REGISTER | --- | FLAGS
4457 | 17 | 105 | DERATING CONTROL 14 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4458 | 17 | 106 | DERATING CONTROL 15 - Input measure ID | --- | FLAGS
4459 | 17 | 107 | DERATING CONTROL 15 - Control parameter ID | --- | FLAGS
4460 | 17 | 108 | DERATING CONTROL 15 - Input measure START | --- | FLOAT
4461 | 17 | 109 | DERATING CONTROL 15 - Input measure STOP | --- | FLOAT
4462 | 17 | 110 | DERATING CONTROL 15 - Control parameter (Val_STOP / Val_MAX) | --- | FLOAT
4463 | 17 | 111 | DERATING CONTROL 15 - CONFIGURATION REGISTER | --- | FLAGS
4464 | 17 | 112 | DERATING CONTROL 15 - Control parameter ramp (Val_DELTA / s) | --- | FLOAT
4608 | 18 | 0 | THERMAL PROTECTION DISABLE REGISTER | --- | FLAGS
4609 | 18 | 1 | THERMAL PROTECTION 0 - Input measure ID | --- | FLAGS
4610 | 18 | 2 | THERMAL PROTECTION 0 - OTH | °C | FLOAT
4611 | 18 | 3 | THERMAL PROTECTION 0 - Restore from OTH hysteresis | °C | FLOAT
4612 | 18 | 4 | THERMAL PROTECTION 0 - UTH | °C | FLOAT
4613 | 18 | 5 | THERMAL PROTECTION 0 - Restore from UTH hysteresis | °C | FLOAT
4614 | 18 | 6 | THERMAL PROTECTION 1 - Input measure ID | --- | FLAGS
4615 | 18 | 7 | THERMAL PROTECTION 1 - OTH | °C | FLOAT
4616 | 18 | 8 | THERMAL PROTECTION 1 - Restore from OTH hysteresis | °C | FLOAT
4617 | 18 | 9 | THERMAL PROTECTION 1 - UTH | °C | FLOAT
4618 | 18 | 10 | THERMAL PROTECTION 1 - Restore from UTH hysteresis | °C | FLOAT
4619 | 18 | 11 | THERMAL PROTECTION 2 - Input measure ID | --- | FLAGS
4620 | 18 | 12 | THERMAL PROTECTION 2 - OTH | °C | FLOAT
4621 | 18 | 13 | THERMAL PROTECTION 2 - Restore from OTH hysteresis | °C | FLOAT
4622 | 18 | 14 | THERMAL PROTECTION 2 - UTH | °C | FLOAT
4623 | 18 | 15 | THERMAL PROTECTION 2 - Restore from UTH hysteresis | °C | FLOAT
4624 | 18 | 16 | THERMAL PROTECTION 3 - Input measure ID | --- | FLAGS
4625 | 18 | 17 | THERMAL PROTECTION 3 - OTH | °C | FLOAT
4626 | 18 | 18 | THERMAL PROTECTION 3 - Restore from OTH hysteresis | °C | FLOAT
4627 | 18 | 19 | THERMAL PROTECTION 3 - UTH | °C | FLOAT
4628 | 18 | 20 | THERMAL PROTECTION 3 - Restore from UTH hysteresis | °C | FLOAT
4629 | 18 | 21 | THERMAL PROTECTION 4 - Input measure ID | --- | FLAGS
4630 | 18 | 22 | THERMAL PROTECTION 4 - OTH | °C | FLOAT
4631 | 18 | 23 | THERMAL PROTECTION 4 - Restore from OTH hysteresis | °C | FLOAT
4632 | 18 | 24 | THERMAL PROTECTION 4 - UTH | °C | FLOAT
4633 | 18 | 25 | THERMAL PROTECTION 4 - Restore from UTH hysteresis | °C | FLOAT
4634 | 18 | 26 | THERMAL PROTECTION 5 - Input measure ID | --- | FLAGS
4635 | 18 | 27 | THERMAL PROTECTION 5 - OTH | °C | FLOAT
4636 | 18 | 28 | THERMAL PROTECTION 5 - Restore from OTH hysteresis | °C | FLOAT
4637 | 18 | 29 | THERMAL PROTECTION 5 - UTH | °C | FLOAT
4638 | 18 | 30 | THERMAL PROTECTION 5 - Restore from UTH hysteresis | °C | FLOAT
4639 | 18 | 31 | THERMAL PROTECTION 6 - Input measure ID | --- | FLAGS
4640 | 18 | 32 | THERMAL PROTECTION 6 - OTH | °C | FLOAT
4641 | 18 | 33 | THERMAL PROTECTION 6 - Restore from OTH hysteresis | °C | FLOAT
4642 | 18 | 34 | THERMAL PROTECTION 6 - UTH | °C | FLOAT
4643 | 18 | 35 | THERMAL PROTECTION 6 - Restore from UTH hysteresis | °C | FLOAT
4644 | 18 | 36 | THERMAL PROTECTION 7 - Input measure ID | --- | FLAGS
4645 | 18 | 37 | THERMAL PROTECTION 7 - OTH | °C | FLOAT
4646 | 18 | 38 | THERMAL PROTECTION 7 - Restore from OTH hysteresis | °C | FLOAT
4647 | 18 | 39 | THERMAL PROTECTION 7 - UTH | °C | FLOAT
4648 | 18 | 40 | THERMAL PROTECTION 7 - Restore from UTH hysteresis | °C | FLOAT
4649 | 18 | 41 | THERMAL PROTECTION 8 - Input measure ID | --- | FLAGS
4650 | 18 | 42 | THERMAL PROTECTION 8 - OTH | °C | FLOAT
4651 | 18 | 43 | THERMAL PROTECTION 8 - Restore from OTH hysteresis | °C | FLOAT
4652 | 18 | 44 | THERMAL PROTECTION 8 - UTH | °C | FLOAT
4653 | 18 | 45 | THERMAL PROTECTION 8 - Restore from UTH hysteresis | °C | FLOAT
4654 | 18 | 46 | THERMAL PROTECTION 9 - Input measure ID | --- | FLAGS
4655 | 18 | 47 | THERMAL PROTECTION 9 - OTH | °C | FLOAT
4656 | 18 | 48 | THERMAL PROTECTION 9 - Restore from OTH hysteresis | °C | FLOAT
4657 | 18 | 49 | THERMAL PROTECTION 9 - UTH | °C | FLOAT
4658 | 18 | 50 | THERMAL PROTECTION 9 - Restore from UTH hysteresis | °C | FLOAT
4659 | 18 | 51 | THERMAL PROTECTION 10 - Input measure ID | --- | FLAGS
4660 | 18 | 52 | THERMAL PROTECTION 10 - OTH | °C | FLOAT
4661 | 18 | 53 | THERMAL PROTECTION 10 - Restore from OTH hysteresis | °C | FLOAT
4662 | 18 | 54 | THERMAL PROTECTION 10 - UTH | °C | FLOAT
4663 | 18 | 55 | THERMAL PROTECTION 10 - Restore from UTH hysteresis | °C | FLOAT
4664 | 18 | 56 | THERMAL PROTECTION 11 - Input measure ID | --- | FLAGS
4665 | 18 | 57 | THERMAL PROTECTION 11 - OTH | °C | FLOAT
4666 | 18 | 58 | THERMAL PROTECTION 11 - Restore from OTH hysteresis | °C | FLOAT
4667 | 18 | 59 | THERMAL PROTECTION 11 - UTH | °C | FLOAT
4668 | 18 | 60 | THERMAL PROTECTION 11 - Restore from UTH hysteresis | °C | FLOAT
4669 | 18 | 61 | THERMAL PROTECTION 12 - Input measure ID | --- | FLAGS
4670 | 18 | 62 | THERMAL PROTECTION 12 - OTH | °C | FLOAT
4671 | 18 | 63 | THERMAL PROTECTION 12 - Restore from OTH hysteresis | °C | FLOAT
4672 | 18 | 64 | THERMAL PROTECTION 12 - UTH | °C | FLOAT
4673 | 18 | 65 | THERMAL PROTECTION 12 - Restore from UTH hysteresis | °C | FLOAT
4674 | 18 | 66 | THERMAL PROTECTION 13 - Input measure ID | --- | FLAGS
4675 | 18 | 67 | THERMAL PROTECTION 13 - OTH | °C | FLOAT
4676 | 18 | 68 | THERMAL PROTECTION 13 - Restore from OTH hysteresis | °C | FLOAT
4677 | 18 | 69 | THERMAL PROTECTION 13 - UTH | °C | FLOAT
4678 | 18 | 70 | THERMAL PROTECTION 13 - Restore from UTH hysteresis | °C | FLOAT
4679 | 18 | 71 | THERMAL PROTECTION 14 - Input measure ID | --- | FLAGS
4680 | 18 | 72 | THERMAL PROTECTION 14 - OTH | °C | FLOAT
4681 | 18 | 73 | THERMAL PROTECTION 14 - Restore from OTH hysteresis | °C | FLOAT
4682 | 18 | 74 | THERMAL PROTECTION 14 - UTH | °C | FLOAT
4683 | 18 | 75 | THERMAL PROTECTION 14 - Restore from UTH hysteresis | °C | FLOAT
4684 | 18 | 76 | THERMAL PROTECTION 15 - Input measure ID | --- | FLAGS
4685 | 18 | 77 | THERMAL PROTECTION 15 - OTH | °C | FLOAT
4686 | 18 | 78 | THERMAL PROTECTION 15 - Restore from OTH hysteresis | °C | FLOAT
4687 | 18 | 79 | THERMAL PROTECTION 15 - UTH | °C | FLOAT
4688 | 18 | 80 | THERMAL PROTECTION 15 - Restore from UTH hysteresis | °C | FLOAT
4864 | 19 | 0 | FAN DISABLE REGISTER | --- | FLAGS
4865 | 19 | 1 | FAN CONTROL 0 - Fan command owner ID | --- | FLAGS
4866 | 19 | 2 | FAN CONTROL 0 - Input measure ID | --- | FLAGS
4867 | 19 | 3 | FAN CONTROL 0 - Output speed ID | --- | FLAGS
4868 | 19 | 4 | FAN CONTROL 0 - Input measure MIN for fan start | --- | FLOAT
4869 | 19 | 5 | FAN CONTROL 0 - Input measure MAX for fan start | --- | FLOAT
4870 | 19 | 6 | FAN CONTROL 0 - Input Measure Hysteresis | --- | FLOAT
4871 | 19 | 7 | FAN CONTROL 0 - Speed MIN for fan fault | rpm | FLOAT
4872 | 19 | 8 | FAN CONTROL 1 - Fan command owner ID | --- | FLAGS
4873 | 19 | 9 | FAN CONTROL 1 - Input measure ID | --- | FLAGS
4874 | 19 | 10 | FAN CONTROL 1 - Output speed ID | --- | FLAGS
4875 | 19 | 11 | FAN CONTROL 1 - Input measure MIN for fan start | --- | FLOAT
4876 | 19 | 12 | FAN CONTROL 1 - Input measure MAX for fan start | --- | FLOAT
4877 | 19 | 13 | FAN CONTROL 1 - Input Measure Hysteresis | --- | FLOAT
4878 | 19 | 14 | FAN CONTROL 1 - Speed MIN for fan fault | rpm | FLOAT
4879 | 19 | 15 | FAN CONTROL 2 - Fan command owner ID | --- | FLAGS
4880 | 19 | 16 | FAN CONTROL 2 - Input measure ID | --- | FLAGS
4881 | 19 | 17 | FAN CONTROL 2 - Output speed ID | --- | FLAGS
4882 | 19 | 18 | FAN CONTROL 2 - Input measure MIN for fan start | --- | FLOAT
4883 | 19 | 19 | FAN CONTROL 2 - Input measure MAX for fan start | --- | FLOAT
4884 | 19 | 20 | FAN CONTROL 2 - Input Measure Hysteresis | --- | FLOAT
4885 | 19 | 21 | FAN CONTROL 2 - Speed MIN for fan fault | rpm | FLOAT
4886 | 19 | 22 | FAN CONTROL 3 - Fan command owner ID | --- | FLAGS
4887 | 19 | 23 | FAN CONTROL 3 - Input measure ID | --- | FLAGS
4888 | 19 | 24 | FAN CONTROL 3 - Output speed ID | --- | FLAGS
4889 | 19 | 25 | FAN CONTROL 3 - Input measure MIN for fan start | --- | FLOAT
4890 | 19 | 26 | FAN CONTROL 3 - Input measure MAX for fan start | --- | FLOAT
4891 | 19 | 27 | FAN CONTROL 3 - Input Measure Hysteresis | --- | FLOAT
4892 | 19 | 28 | FAN CONTROL 3 - Speed MIN for fan fault | rpm | FLOAT
4893 | 19 | 29 | FAN CONTROL 4 - Fan command owner ID | --- | FLAGS
4894 | 19 | 30 | FAN CONTROL 4 - Input measure ID | --- | FLAGS
4895 | 19 | 31 | FAN CONTROL 4 - Output speed ID | --- | FLAGS
4896 | 19 | 32 | FAN CONTROL 4 - Input measure MIN for fan start | --- | FLOAT
4897 | 19 | 33 | FAN CONTROL 4 - Input measure MAX for fan start | --- | FLOAT
4898 | 19 | 34 | FAN CONTROL 4 - Input Measure Hysteresis | --- | FLOAT
4899 | 19 | 35 | FAN CONTROL 4 - Speed MIN for fan fault | rpm | FLOAT
4900 | 19 | 36 | FAN CONTROL 5 - Fan command owner ID | --- | FLAGS
4901 | 19 | 37 | FAN CONTROL 5 - Input measure ID | --- | FLAGS
4902 | 19 | 38 | FAN CONTROL 5 - Output speed ID | --- | FLAGS
4903 | 19 | 39 | FAN CONTROL 5 - Input measure MIN for fan start | --- | FLOAT
4904 | 19 | 40 | FAN CONTROL 5 - Input measure MAX for fan start | --- | FLOAT
4905 | 19 | 41 | FAN CONTROL 5 - Input Measure Hysteresis | --- | FLOAT
4906 | 19 | 42 | FAN CONTROL 5 - Speed MIN for fan fault | rpm | FLOAT
4907 | 19 | 43 | FAN CONTROL 6 - Fan command owner ID | --- | FLAGS
4908 | 19 | 44 | FAN CONTROL 6 - Input measure ID | --- | FLAGS
4909 | 19 | 45 | FAN CONTROL 6 - Output speed ID | --- | FLAGS
4910 | 19 | 46 | FAN CONTROL 6 - Input measure MIN for fan start | --- | FLOAT
4911 | 19 | 47 | FAN CONTROL 6 - Input measure MAX for fan start | --- | FLOAT
4912 | 19 | 48 | FAN CONTROL 6 - Input Measure Hysteresis | --- | FLOAT
4913 | 19 | 49 | FAN CONTROL 6 - Speed MIN for fan fault | rpm | FLOAT
4914 | 19 | 50 | FAN CONTROL 7 - Fan command owner ID | --- | FLAGS
4915 | 19 | 51 | FAN CONTROL 7 - Input measure ID | --- | FLAGS
4916 | 19 | 52 | FAN CONTROL 7 - Output speed ID | --- | FLAGS
4917 | 19 | 53 | FAN CONTROL 7 - Input measure MIN for fan start | --- | FLOAT
4918 | 19 | 54 | FAN CONTROL 7 - Input measure MAX for fan start | --- | FLOAT
4919 | 19 | 55 | FAN CONTROL 7 - Input Measure Hysteresis | --- | FLOAT
4920 | 19 | 56 | FAN CONTROL 7 - Speed MIN for fan fault | rpm | FLOAT
4921 | 19 | 57 | FAN CONTROL 8 - Fan command owner ID | --- | FLAGS
4922 | 19 | 58 | FAN CONTROL 8 - Input measure ID | --- | FLAGS
4923 | 19 | 59 | FAN CONTROL 8 - Output speed ID | --- | FLAGS
4924 | 19 | 60 | FAN CONTROL 8 - Input measure MIN for fan start | --- | FLOAT
4925 | 19 | 61 | FAN CONTROL 8 - Input measure MAX for fan start | --- | FLOAT
4926 | 19 | 62 | FAN CONTROL 8 - Input Measure Hysteresis | --- | FLOAT
4927 | 19 | 63 | FAN CONTROL 8 - Speed MIN for fan fault | rpm | FLOAT
4928 | 19 | 64 | FAN CONTROL 9 - Fan command owner ID | --- | FLAGS
4929 | 19 | 65 | FAN CONTROL 9 - Input measure ID | --- | FLAGS
4930 | 19 | 66 | FAN CONTROL 9 - Output speed ID | --- | FLAGS
4931 | 19 | 67 | FAN CONTROL 9 - Input measure MIN for fan start | --- | FLOAT
4932 | 19 | 68 | FAN CONTROL 9 - Input measure MAX for fan start | --- | FLOAT
4933 | 19 | 69 | FAN CONTROL 9 - Input Measure Hysteresis | --- | FLOAT
4934 | 19 | 70 | FAN CONTROL 9 - Speed MIN for fan fault | rpm | FLOAT
4935 | 19 | 71 | FAN CONTROL 10 - Fan command owner ID | --- | FLAGS
4936 | 19 | 72 | FAN CONTROL 10 - Input measure ID | --- | FLAGS
4937 | 19 | 73 | FAN CONTROL 10 - Output speed ID | --- | FLAGS
4938 | 19 | 74 | FAN CONTROL 10 - Input measure MIN for fan start | --- | FLOAT
4939 | 19 | 75 | FAN CONTROL 10 - Input measure MAX for fan start | --- | FLOAT
4940 | 19 | 76 | FAN CONTROL 10 - Input Measure Hysteresis | --- | FLOAT
4941 | 19 | 77 | FAN CONTROL 10 - Speed MIN for fan fault | rpm | FLOAT
4942 | 19 | 78 | FAN CONTROL 11 - Fan command owner ID | --- | FLAGS
4943 | 19 | 79 | FAN CONTROL 11 - Input measure ID | --- | FLAGS
4944 | 19 | 80 | FAN CONTROL 11 - Output speed ID | --- | FLAGS
4945 | 19 | 81 | FAN CONTROL 11 - Input measure MIN for fan start | --- | FLOAT
4946 | 19 | 82 | FAN CONTROL 11 - Input measure MAX for fan start | --- | FLOAT
4947 | 19 | 83 | FAN CONTROL 11 - Input Measure Hysteresis | --- | FLOAT
4948 | 19 | 84 | FAN CONTROL 11 - Speed MIN for fan fault | rpm | FLOAT
4949 | 19 | 85 | FAN CONTROL 12 - Fan command owner ID | --- | FLAGS
4950 | 19 | 86 | FAN CONTROL 12 - Input measure ID | --- | FLAGS
4951 | 19 | 87 | FAN CONTROL 12 - Output speed ID | --- | FLAGS
4952 | 19 | 88 | FAN CONTROL 12 - Input measure MIN for fan start | --- | FLOAT
4953 | 19 | 89 | FAN CONTROL 12 - Input measure MAX for fan start | --- | FLOAT
4954 | 19 | 90 | FAN CONTROL 12 - Input Measure Hysteresis | --- | FLOAT
4955 | 19 | 91 | FAN CONTROL 12 - Speed MIN for fan fault | rpm | FLOAT
4956 | 19 | 92 | FAN CONTROL 13 - Fan command owner ID | --- | FLAGS
4957 | 19 | 93 | FAN CONTROL 13 - Input measure ID | --- | FLAGS
4958 | 19 | 94 | FAN CONTROL 13 - Output speed ID | --- | FLAGS
4959 | 19 | 95 | FAN CONTROL 13 - Input measure MIN for fan start | --- | FLOAT
4960 | 19 | 96 | FAN CONTROL 13 - Input measure MAX for fan start | --- | FLOAT
4961 | 19 | 97 | FAN CONTROL 13 - Input Measure Hysteresis | --- | FLOAT
4962 | 19 | 98 | FAN CONTROL 13 - Speed MIN for fan fault | rpm | FLOAT
4963 | 19 | 99 | FAN CONTROL 14 - Fan command owner ID | --- | FLAGS
4964 | 19 | 100 | FAN CONTROL 14 - Input measure ID | --- | FLAGS
4965 | 19 | 101 | FAN CONTROL 14 - Output speed ID | --- | FLAGS
4966 | 19 | 102 | FAN CONTROL 14 - Input measure MIN for fan start | --- | FLOAT
4967 | 19 | 103 | FAN CONTROL 14 - Input measure MAX for fan start | --- | FLOAT
4968 | 19 | 104 | FAN CONTROL 14 - Input Measure Hysteresis | --- | FLOAT
4969 | 19 | 105 | FAN CONTROL 14 - Speed MIN for fan fault | rpm | FLOAT
4970 | 19 | 106 | FAN CONTROL 15 - Fan command owner ID | --- | FLAGS
4971 | 19 | 107 | FAN CONTROL 15 - Input measure ID | --- | FLAGS
4972 | 19 | 108 | FAN CONTROL 15 - Output speed ID | --- | FLAGS
4973 | 19 | 109 | FAN CONTROL 15 - Input measure MIN for fan start | --- | FLOAT
4974 | 19 | 110 | FAN CONTROL 15 - Input measure MAX for fan start | --- | FLOAT
4975 | 19 | 111 | FAN CONTROL 15 - Input Measure Hysteresis | --- | FLOAT
4976 | 19 | 112 | FAN CONTROL 15 - Speed MIN for fan fault | rpm | FLOAT
5120 | 20 | 0 | SERIAL LINK DISABLE REGISTER | --- | FLAGS
5121 | 20 | 1 | SERIAL LINK 0 - Node address | --- | UI8
5122 | 20 | 2 | SERIAL LINK 0 - Baud-rate code | --- | UI32
5123 | 20 | 3 | SERIAL LINK 0 - Protocol code | --- | UI32
5124 | 20 | 4 | SERIAL LINK 0 - Parity mode | --- | UI32
5125 | 20 | 5 | SERIAL LINK 1 - Node address | --- | UI8
5126 | 20 | 6 | SERIAL LINK 1 - Baud-rate code | --- | UI32
5127 | 20 | 7 | SERIAL LINK 1 - Protocol code | --- | UI32
5128 | 20 | 8 | SERIAL LINK 1 - Parity mode | --- | UI32
5376 | 21 | 0 | DIGITAL INPUT DISABLE REGISTER | --- | FLAGS
5377 | 21 | 1 | DIGITAL INPUT 0 - MODE | --- | UI32
5378 | 21 | 2 | DIGITAL INPUT 0 - DEBOUNCING FILTER | ms | UI32
5379 | 21 | 3 | DIGITAL INPUT 0 - TRIGGER TYPE | --- | FLAGS
5380 | 21 | 4 | DIGITAL INPUT 1 - MODE | --- | UI32
5381 | 21 | 5 | DIGITAL INPUT 1 - DEBOUNCING FILTER | ms | UI32
5382 | 21 | 6 | DIGITAL INPUT 1 - TRIGGER TYPE | --- | FLAGS
5383 | 21 | 7 | DIGITAL INPUT 2 - MODE | --- | UI32
5384 | 21 | 8 | DIGITAL INPUT 2 - DEBOUNCING FILTER | ms | UI32
5385 | 21 | 9 | DIGITAL INPUT 2 - TRIGGER TYPE | --- | FLAGS
5386 | 21 | 10 | DIGITAL INPUT 3 - MODE | --- | UI32
5387 | 21 | 11 | DIGITAL INPUT 3 - DEBOUNCING FILTER | ms | UI32
5388 | 21 | 12 | DIGITAL INPUT 3 - TRIGGER TYPE | --- | FLAGS
5389 | 21 | 13 | DIGITAL INPUT 4 - MODE | --- | UI32
5390 | 21 | 14 | DIGITAL INPUT 4 - DEBOUNCING FILTER | ms | UI32
5391 | 21 | 15 | DIGITAL INPUT 4 - TRIGGER TYPE | --- | FLAGS
5392 | 21 | 16 | DIGITAL INPUT 5 - MODE | --- | UI32
5393 | 21 | 17 | DIGITAL INPUT 5 - DEBOUNCING FILTER | ms | UI32
5394 | 21 | 18 | DIGITAL INPUT 5 - TRIGGER TYPE | --- | FLAGS
5395 | 21 | 19 | DIGITAL INPUT 6 - MODE | --- | UI32
5396 | 21 | 20 | DIGITAL INPUT 6 - DEBOUNCING FILTER | ms | UI32
5397 | 21 | 21 | DIGITAL INPUT 6 - TRIGGER TYPE | --- | FLAGS
5398 | 21 | 22 | DIGITAL INPUT 7 - MODE | --- | UI32
5399 | 21 | 23 | DIGITAL INPUT 7 - DEBOUNCING FILTER | ms | UI32
5400 | 21 | 24 | DIGITAL INPUT 7 - TRIGGER TYPE | --- | FLAGS
5401 | 21 | 25 | DIGITAL INPUT 8 - MODE | --- | UI32
5402 | 21 | 26 | DIGITAL INPUT 8 - DEBOUNCING FILTER | ms | UI32
5403 | 21 | 27 | DIGITAL INPUT 8 - TRIGGER TYPE | --- | FLAGS
5404 | 21 | 28 | DIGITAL INPUT 9 - MODE | --- | UI32
5405 | 21 | 29 | DIGITAL INPUT 9 - DEBOUNCING FILTER | ms | UI32
5406 | 21 | 30 | DIGITAL INPUT 9 - TRIGGER TYPE | --- | FLAGS
5407 | 21 | 31 | DIGITAL INPUT 10 - MODE | --- | UI32
5408 | 21 | 32 | DIGITAL INPUT 10 - DEBOUNCING FILTER | ms | UI32
5409 | 21 | 33 | DIGITAL INPUT 10 - TRIGGER TYPE | --- | FLAGS
5410 | 21 | 34 | DIGITAL INPUT 11 - MODE | --- | UI32
5411 | 21 | 35 | DIGITAL INPUT 11 - DEBOUNCING FILTER | ms | UI32
5412 | 21 | 36 | DIGITAL INPUT 11 - TRIGGER TYPE | --- | FLAGS
5413 | 21 | 37 | DIGITAL INPUT 12 - MODE | --- | UI32
5414 | 21 | 38 | DIGITAL INPUT 12 - DEBOUNCING FILTER | ms | UI32
5415 | 21 | 39 | DIGITAL INPUT 12 - TRIGGER TYPE | --- | FLAGS
5416 | 21 | 40 | DIGITAL INPUT 13 - MODE | --- | UI32
5417 | 21 | 41 | DIGITAL INPUT 13 - DEBOUNCING FILTER | ms | UI32
5418 | 21 | 42 | DIGITAL INPUT 13 - TRIGGER TYPE | --- | FLAGS
5419 | 21 | 43 | DIGITAL INPUT 14 - MODE | --- | UI32
5420 | 21 | 44 | DIGITAL INPUT 14 - DEBOUNCING FILTER | ms | UI32
5421 | 21 | 45 | DIGITAL INPUT 14 - TRIGGER TYPE | --- | FLAGS
5422 | 21 | 46 | DIGITAL INPUT 15 - MODE | --- | UI32
5423 | 21 | 47 | DIGITAL INPUT 15 - DEBOUNCING FILTER | ms | UI32
5424 | 21 | 48 | DIGITAL INPUT 15 - TRIGGER TYPE | --- | FLAGS
5504 | 21 | 128 | DIGITAL OUTPUT DISABLE REGISTER | --- | FLAGS
5505 | 21 | 129 | DIGITAL OUTPUT 0 - MODE | --- | UI32
5506 | 21 | 130 | DIGITAL OUTPUT 0 - (reserved 0) | --- | UI32
5507 | 21 | 131 | DIGITAL OUTPUT 0 - (reserved 1) | --- | UI32
5508 | 21 | 132 | DIGITAL OUTPUT 1 - MODE | --- | UI32
5509 | 21 | 133 | DIGITAL OUTPUT 1 - (reserved 0) | --- | UI32
5510 | 21 | 134 | DIGITAL OUTPUT 1 - (reserved 1) | --- | UI32
5511 | 21 | 135 | DIGITAL OUTPUT 2 - MODE | --- | UI32
5512 | 21 | 136 | DIGITAL OUTPUT 2 - (reserved 0) | --- | UI32
5513 | 21 | 137 | DIGITAL OUTPUT 2 - (reserved 1) | --- | UI32
5514 | 21 | 138 | DIGITAL OUTPUT 3 - MODE | --- | UI32
5515 | 21 | 139 | DIGITAL OUTPUT 3 - (reserved 0) | --- | UI32
5516 | 21 | 140 | DIGITAL OUTPUT 3 - (reserved 1) | --- | UI32
5517 | 21 | 141 | DIGITAL OUTPUT 4 - MODE | --- | UI32
5518 | 21 | 142 | DIGITAL OUTPUT 4 - (reserved 0) | --- | UI32
5519 | 21 | 143 | DIGITAL OUTPUT 4 - (reserved 1) | --- | UI32
5520 | 21 | 144 | DIGITAL OUTPUT 5 - MODE | --- | UI32
5521 | 21 | 145 | DIGITAL OUTPUT 5 - (reserved 0) | --- | UI32
5522 | 21 | 146 | DIGITAL OUTPUT 5 - (reserved 1) | --- | UI32
5523 | 21 | 147 | DIGITAL OUTPUT 6 - MODE | --- | UI32
5524 | 21 | 148 | DIGITAL OUTPUT 6 - (reserved 0) | --- | UI32
5525 | 21 | 149 | DIGITAL OUTPUT 6 - (reserved 1) | --- | UI32
5526 | 21 | 150 | DIGITAL OUTPUT 7 - MODE | --- | UI32
5527 | 21 | 151 | DIGITAL OUTPUT 7 - (reserved 0) | --- | UI32
5528 | 21 | 152 | DIGITAL OUTPUT 7 - (reserved 1) | --- | UI32
5529 | 21 | 153 | DIGITAL OUTPUT 8 - MODE | --- | UI32
5530 | 21 | 154 | DIGITAL OUTPUT 8 - (reserved 0) | --- | UI32
5531 | 21 | 155 | DIGITAL OUTPUT 8 - (reserved 1) | --- | UI32
5532 | 21 | 156 | DIGITAL OUTPUT 9 - MODE | --- | UI32
5533 | 21 | 157 | DIGITAL OUTPUT 9 - (reserved 0) | --- | UI32
5534 | 21 | 158 | DIGITAL OUTPUT 9 - (reserved 1) | --- | UI32
5535 | 21 | 159 | DIGITAL OUTPUT 10 - MODE | --- | UI32
5536 | 21 | 160 | DIGITAL OUTPUT 10 - (reserved 0) | --- | UI32
5537 | 21 | 161 | DIGITAL OUTPUT 10 - (reserved 1) | --- | UI32
5538 | 21 | 162 | DIGITAL OUTPUT 11 - MODE | --- | UI32
5539 | 21 | 163 | DIGITAL OUTPUT 11 - (reserved 0) | --- | UI32
5540 | 21 | 164 | DIGITAL OUTPUT 11 - (reserved 1) | --- | UI32
5541 | 21 | 165 | DIGITAL OUTPUT 12 - MODE | --- | UI32
5542 | 21 | 166 | DIGITAL OUTPUT 12 - (reserved 0) | --- | UI32
5543 | 21 | 167 | DIGITAL OUTPUT 12 - (reserved 1) | --- | UI32
5544 | 21 | 168 | DIGITAL OUTPUT 13 - MODE | --- | UI32
5545 | 21 | 169 | DIGITAL OUTPUT 13 - (reserved 0) | --- | UI32
5546 | 21 | 170 | DIGITAL OUTPUT 13 - (reserved 1) | --- | UI32
5547 | 21 | 171 | DIGITAL OUTPUT 14 - MODE | --- | UI32
5548 | 21 | 172 | DIGITAL OUTPUT 14 - (reserved 0) | --- | UI32
5549 | 21 | 173 | DIGITAL OUTPUT 14 - (reserved 1) | --- | UI32
5550 | 21 | 174 | DIGITAL OUTPUT 15 - MODE | --- | UI32
5551 | 21 | 175 | DIGITAL OUTPUT 15 - (reserved 0) | --- | UI32
5552 | 21 | 176 | DIGITAL OUTPUT 15 - (reserved 1) | --- | UI32
5632 | 22 | 0 | ACTIVE POWER CONTROL CONFIGURATION REGISTER | --- | FLAGS
5633 | 22 | 1 | P MODE (static) | --- | UI32
5634 | 22 | 2 | P/Pmax SET-POINT (static) | --- | FLOAT
5635 | 22 | 3 | P SMOOTH TIME (static) | ms | UI32
5636 | 22 | 4 | P SMOOTH MODE (static) | --- | UI32
5888 | 23 | 0 | REACTIVE POWER CONTROL CONFIGURATION REGISTER | --- | FLAGS
5889 | 23 | 1 | Q MODE (static) | --- | UI32
5890 | 23 | 2 | Q/Qmax SET-POINT (static) | --- | FLOAT
5891 | 23 | 3 | Q SMOOTH TIME (static) | ms | UI32
5892 | 23 | 4 | Q SMOOTH MODE (static) | --- | UI32
5893 | 23 | 5 | V/Vnom for lock-in ( cos-phi=f(P) mode ) | --- | FLOAT
5894 | 23 | 6 | V/Vnom for lock-out ( cos-phi=f(P) mode ) | --- | FLOAT
5895 | 23 | 7 | P/Pnom for lock-in ( Q=f(U) mode ) | --- | FLOAT
5896 | 23 | 8 | P/Pnom for lock-out ( Q=f(U) mode ) | --- | FLOAT
5897 | 23 | 9 | Intentional delay (Q=f(U) mode) | ms | UI32
5908 | 23 | 20 | K Output Capacitor Compensation | --- | FLOAT
5909 | 23 | 21 | Q Output Capacitor Compensation | nF | FLOAT
6016 | 23 | 128 | Cos-phi=f(U) - X Point 0 (P/Pnom) | --- | FLOAT
6017 | 23 | 129 | Cos-phi=f(U) - Y Point 0 (cos-phi) | --- | FLOAT
6018 | 23 | 130 | Cos-phi=f(U) - X Point 1 (P/Pnom) | --- | FLOAT
6019 | 23 | 131 | Cos-phi=f(U) - Y Point 1 (cos-phi) | --- | FLOAT
6020 | 23 | 132 | Cos-phi=f(U) - X Point 2 (P/Pnom) | --- | FLOAT
6021 | 23 | 133 | Cos-phi=f(U) - Y Point 2 (cos-phi) | --- | FLOAT
6022 | 23 | 134 | Cos-phi=f(U) - X Point 3 (P/Pnom) | --- | FLOAT
6023 | 23 | 135 | Cos-phi=f(U) - Y Point 3 (cos-phi) | --- | FLOAT
6024 | 23 | 136 | Cos-phi=f(U) - X Point 4 (P/Pnom) | --- | FLOAT
6025 | 23 | 137 | Cos-phi=f(U) - Y Point 4 (cos-phi) | --- | FLOAT
6026 | 23 | 138 | Cos-phi=f(U) - X Point 5 (P/Pnom) | --- | FLOAT
6027 | 23 | 139 | Cos-phi=f(U) - Y Point 5 (cos-phi) | --- | FLOAT
6028 | 23 | 140 | Cos-phi=f(U) - X Point 6 (P/Pnom) | --- | FLOAT
6029 | 23 | 141 | Cos-phi=f(U) - Y Point 6 (cos-phi) | --- | FLOAT
6030 | 23 | 142 | Cos-phi=f(U) - X Point 7 (P/Pnom) | --- | FLOAT
6031 | 23 | 143 | Cos-phi=f(U) - Y Point 7 (cos-phi) | --- | FLOAT
6032 | 23 | 144 | Cos-phi=f(U) - X Point 8 (P/Pnom) | --- | FLOAT
6033 | 23 | 145 | Cos-phi=f(U) - Y Point 8 (cos-phi) | --- | FLOAT
6034 | 23 | 146 | Cos-phi=f(U) - X Point 9 (P/Pnom) | --- | FLOAT
6035 | 23 | 147 | Cos-phi=f(U) - Y Point 9 (cos-phi) | --- | FLOAT
6036 | 23 | 148 | Cos-phi=f(U) - X Point 10 (P/Pnom) | --- | FLOAT
6037 | 23 | 149 | Cos-phi=f(U) - Y Point 10 (cos-phi) | --- | FLOAT
6038 | 23 | 150 | Cos-phi=f(U) - X Point 11 (P/Pnom) | --- | FLOAT
6039 | 23 | 151 | Cos-phi=f(U) - Y Point 11 (cos-phi) | --- | FLOAT
6040 | 23 | 152 | Cos-phi=f(U) - X Point 12 (P/Pnom) | --- | FLOAT
6041 | 23 | 153 | Cos-phi=f(U) - Y Point 12 (cos-phi) | --- | FLOAT
6042 | 23 | 154 | Cos-phi=f(U) - X Point 13 (P/Pnom) | --- | FLOAT
6043 | 23 | 155 | Cos-phi=f(U) - Y Point 13 (cos-phi) | --- | FLOAT
6044 | 23 | 156 | Cos-phi=f(U) - X Point 14 (P/Pnom) | --- | FLOAT
6045 | 23 | 157 | Cos-phi=f(U) - Y Point 14 (cos-phi) | --- | FLOAT
6046 | 23 | 158 | Cos-phi=f(U) - X Point 15 (P/Pnom) | --- | FLOAT
6047 | 23 | 159 | Cos-phi=f(U) - Y Point 15 (cos-phi) | --- | FLOAT
6048 | 23 | 160 | Q=f(U) - X Point 0 (U/Unom) | --- | FLOAT
6049 | 23 | 161 | Q=f(U) - Y Point 0 (Q) | --- | FLOAT
6050 | 23 | 162 | Q=f(U) - X Point 1 (U/Unom) | --- | FLOAT
6051 | 23 | 163 | Q=f(U) - Y Point 1 (Q) | --- | FLOAT
6052 | 23 | 164 | Q=f(U) - X Point 2 (U/Unom) | --- | FLOAT
6053 | 23 | 165 | Q=f(U) - Y Point 2 (Q) | --- | FLOAT
6054 | 23 | 166 | Q=f(U) - X Point 3 (U/Unom) | --- | FLOAT
6055 | 23 | 167 | Q=f(U) - Y Point 3 (Q) | --- | FLOAT
6056 | 23 | 168 | Q=f(U) - X Point 4 (U/Unom) | --- | FLOAT
6057 | 23 | 169 | Q=f(U) - Y Point 4 (Q) | --- | FLOAT
6058 | 23 | 170 | Q=f(U) - X Point 5 (U/Unom) | --- | FLOAT
6059 | 23 | 171 | Q=f(U) - Y Point 5 (Q) | --- | FLOAT
6060 | 23 | 172 | Q=f(U) - X Point 6 (U/Unom) | --- | FLOAT
6061 | 23 | 173 | Q=f(U) - Y Point 6 (Q) | --- | FLOAT
6062 | 23 | 174 | Q=f(U) - X Point 7 (U/Unom) | --- | FLOAT
6063 | 23 | 175 | Q=f(U) - Y Point 7 (Q) | --- | FLOAT
6064 | 23 | 176 | Q=f(U) - X Point 8 (U/Unom) | --- | FLOAT
6065 | 23 | 177 | Q=f(U) - Y Point 8 (Q) | --- | FLOAT
6066 | 23 | 178 | Q=f(U) - X Point 9 (U/Unom) | --- | FLOAT
6067 | 23 | 179 | Q=f(U) - Y Point 9 (Q) | --- | FLOAT
6068 | 23 | 180 | Q=f(U) - X Point 10 (U/Unom) | --- | FLOAT
6069 | 23 | 181 | Q=f(U) - Y Point 10 (Q) | --- | FLOAT
6070 | 23 | 182 | Q=f(U) - X Point 11 (U/Unom) | --- | FLOAT
6071 | 23 | 183 | Q=f(U) - Y Point 11 (Q) | --- | FLOAT
6072 | 23 | 184 | Q=f(U) - X Point 12 (U/Unom) | --- | FLOAT
6073 | 23 | 185 | Q=f(U) - Y Point 12 (Q) | --- | FLOAT
6074 | 23 | 186 | Q=f(U) - X Point 13 (U/Unom) | --- | FLOAT
6075 | 23 | 187 | Q=f(U) - Y Point 13 (Q) | --- | FLOAT
6076 | 23 | 188 | Q=f(U) - X Point 14 (U/Unom) | --- | FLOAT
6077 | 23 | 189 | Q=f(U) - Y Point 14 (Q) | --- | FLOAT
6078 | 23 | 190 | Q=f(U) - X Point 15 (U/Unom) | --- | FLOAT
6079 | 23 | 191 | Q=f(U) - Y Point 15 (Q) | --- | FLOAT
6080 | 23 | 192 | Reactive Slot 2 - X Point 0 | --- | FLOAT
6081 | 23 | 193 | Reactive Slot 2 - Y Point 0 | --- | FLOAT
6082 | 23 | 194 | Reactive Slot 2 - X Point 1 | --- | FLOAT
6083 | 23 | 195 | Reactive Slot 2 - Y Point 1 | --- | FLOAT
6084 | 23 | 196 | Reactive Slot 2 - X Point 2 | --- | FLOAT
6085 | 23 | 197 | Reactive Slot 2 - Y Point 2 | --- | FLOAT
6086 | 23 | 198 | Reactive Slot 2 - X Point 3 | --- | FLOAT
6087 | 23 | 199 | Reactive Slot 2 - Y Point 3 | --- | FLOAT
6088 | 23 | 200 | Reactive Slot 2 - X Point 4 | --- | FLOAT
6089 | 23 | 201 | Reactive Slot 2 - Y Point 4 | --- | FLOAT
6090 | 23 | 202 | Reactive Slot 2 - X Point 5 | --- | FLOAT
6091 | 23 | 203 | Reactive Slot 2 - Y Point 5 | --- | FLOAT
6092 | 23 | 204 | Reactive Slot 2 - X Point 6 | --- | FLOAT
6093 | 23 | 205 | Reactive Slot 2 - Y Point 6 | --- | FLOAT
6094 | 23 | 206 | Reactive Slot 2 - X Point 7 | --- | FLOAT
6095 | 23 | 207 | Reactive Slot 2 - Y Point 7 | --- | FLOAT
6096 | 23 | 208 | Reactive Slot 2 - X Point 8 | --- | FLOAT
6097 | 23 | 209 | Reactive Slot 2 - Y Point 8 | --- | FLOAT
6098 | 23 | 210 | Reactive Slot 2 - X Point 9 | --- | FLOAT
6099 | 23 | 211 | Reactive Slot 2 - Y Point 9 | --- | FLOAT
6100 | 23 | 212 | Reactive Slot 2 - X Point 10 | --- | FLOAT
6101 | 23 | 213 | Reactive Slot 2 - Y Point 10 | --- | FLOAT
6102 | 23 | 214 | Reactive Slot 2 - X Point 11 | --- | FLOAT
6103 | 23 | 215 | Reactive Slot 2 - Y Point 11 | --- | FLOAT
6104 | 23 | 216 | Reactive Slot 2 - X Point 12 | --- | FLOAT
6105 | 23 | 217 | Reactive Slot 2 - Y Point 12 | --- | FLOAT
6106 | 23 | 218 | Reactive Slot 2 - X Point 13 | --- | FLOAT
6107 | 23 | 219 | Reactive Slot 2 - Y Point 13 | --- | FLOAT
6108 | 23 | 220 | Reactive Slot 2 - X Point 14 | --- | FLOAT
6109 | 23 | 221 | Reactive Slot 2 - Y Point 14 | --- | FLOAT
6110 | 23 | 222 | Reactive Slot 2 - X Point 15 | --- | FLOAT
6111 | 23 | 223 | Reactive Slot 2 - Y Point 15 | --- | FLOAT
6112 | 23 | 224 | Reactive Slot 3 - X Point 0 | --- | FLOAT
6113 | 23 | 225 | Reactive Slot 3 - Y Point 0 | --- | FLOAT
6114 | 23 | 226 | Reactive Slot 3 - X Point 1 | --- | FLOAT
6115 | 23 | 227 | Reactive Slot 3 - Y Point 1 | --- | FLOAT
6116 | 23 | 228 | Reactive Slot 3 - X Point 2 | --- | FLOAT
6117 | 23 | 229 | Reactive Slot 3 - Y Point 2 | --- | FLOAT
6118 | 23 | 230 | Reactive Slot 3 - X Point 3 | --- | FLOAT
6119 | 23 | 231 | Reactive Slot 3 - Y Point 3 | --- | FLOAT
6120 | 23 | 232 | Reactive Slot 3 - X Point 4 | --- | FLOAT
6121 | 23 | 233 | Reactive Slot 3 - Y Point 4 | --- | FLOAT
6122 | 23 | 234 | Reactive Slot 3 - X Point 5 | --- | FLOAT
6123 | 23 | 235 | Reactive Slot 3 - Y Point 5 | --- | FLOAT
6124 | 23 | 236 | Reactive Slot 3 - X Point 6 | --- | FLOAT
6125 | 23 | 237 | Reactive Slot 3 - Y Point 6 | --- | FLOAT
6126 | 23 | 238 | Reactive Slot 3 - X Point 7 | --- | FLOAT
6127 | 23 | 239 | Reactive Slot 3 - Y Point 7 | --- | FLOAT
6128 | 23 | 240 | Reactive Slot 3 - X Point 8 | --- | FLOAT
6129 | 23 | 241 | Reactive Slot 3 - Y Point 8 | --- | FLOAT
6130 | 23 | 242 | Reactive Slot 3 - X Point 9 | --- | FLOAT
6131 | 23 | 243 | Reactive Slot 3 - Y Point 9 | --- | FLOAT
6132 | 23 | 244 | Reactive Slot 3 - X Point 10 | --- | FLOAT
6133 | 23 | 245 | Reactive Slot 3 - Y Point 10 | --- | FLOAT
6134 | 23 | 246 | Reactive Slot 3 - X Point 11 | --- | FLOAT
6135 | 23 | 247 | Reactive Slot 3 - Y Point 11 | --- | FLOAT
6136 | 23 | 248 | Reactive Slot 3 - X Point 12 | --- | FLOAT
6137 | 23 | 249 | Reactive Slot 3 - Y Point 12 | --- | FLOAT
6138 | 23 | 250 | Reactive Slot 3 - X Point 13 | --- | FLOAT
6139 | 23 | 251 | Reactive Slot 3 - Y Point 13 | --- | FLOAT
6140 | 23 | 252 | Reactive Slot 3 - X Point 14 | --- | FLOAT
6141 | 23 | 253 | Reactive Slot 3 - Y Point 14 | --- | FLOAT
6142 | 23 | 254 | Reactive Slot 3 - X Point 15 | --- | FLOAT
6143 | 23 | 255 | Reactive Slot 3 - Y Point 15 | --- | FLOAT
6144 | 24 | 0 | STANDBY CONFIGURATION REGISTER | --- | FLAGS
6145 | 24 | 1 | STANDBY TOUT | ms | UI32
6400 | 25 | 0 | AFD CONFIGURATION REGISTER | --- | FLAGS
6401 | 25 | 1 | AFD ARC ALARM DETECTION Time Threshold | ms | UI32
6402 | 25 | 2 | AFD GENERIC ALARM Time Threshold | ms | UI32
6403 | 25 | 3 | AFD MIN INPUT CURRENT (to Enable Detection) | A | FLOAT
6656 | 26 | 0 | STATISTICS CONFIGURATION REGISTER | --- | FLAGS
6912 | 27 | 0 | FW REVISION "OFFICIAL" | --- | STRING
7168 | 28 | 0 | ALARM 0 - First Configuration Register | --- | FLAGS
7169 | 28 | 1 | ALARM 0 - Second Configuration Register | --- | FLAGS
7170 | 28 | 2 | ALARM 1 - First Configuration Register | --- | FLAGS
7171 | 28 | 3 | ALARM 1 - Second Configuration Register | --- | FLAGS
7172 | 28 | 4 | ALARM 2 - First Configuration Register | --- | FLAGS
7173 | 28 | 5 | ALARM 2 - Second Configuration Register | --- | FLAGS
7174 | 28 | 6 | ALARM 3 - First Configuration Register | --- | FLAGS
7175 | 28 | 7 | ALARM 3 - Second Configuration Register | --- | FLAGS
7176 | 28 | 8 | ALARM 4 - First Configuration Register | --- | FLAGS
7177 | 28 | 9 | ALARM 4 - Second Configuration Register | --- | FLAGS
7178 | 28 | 10 | ALARM 5 - First Configuration Register | --- | FLAGS
7179 | 28 | 11 | ALARM 5 - Second Configuration Register | --- | FLAGS
7180 | 28 | 12 | ALARM 6 - First Configuration Register | --- | FLAGS
7181 | 28 | 13 | ALARM 6 - Second Configuration Register | --- | FLAGS
7182 | 28 | 14 | ALARM 7 - First Configuration Register | --- | FLAGS
7183 | 28 | 15 | ALARM 7 - Second Configuration Register | --- | FLAGS
7184 | 28 | 16 | ALARM 8 - First Configuration Register | --- | FLAGS
7185 | 28 | 17 | ALARM 8 - Second Configuration Register | --- | FLAGS
7186 | 28 | 18 | ALARM 9 - First Configuration Register | --- | FLAGS
7187 | 28 | 19 | ALARM 9 - Second Configuration Register | --- | FLAGS
7188 | 28 | 20 | ALARM 10 - First Configuration Register | --- | FLAGS
7189 | 28 | 21 | ALARM 10 - Second Configuration Register | --- | FLAGS
7190 | 28 | 22 | ALARM 11 - First Configuration Register | --- | FLAGS
7191 | 28 | 23 | ALARM 11 - Second Configuration Register | --- | FLAGS
7192 | 28 | 24 | ALARM 12 - First Configuration Register | --- | FLAGS
7193 | 28 | 25 | ALARM 12 - Second Configuration Register | --- | FLAGS
7194 | 28 | 26 | ALARM 13 - First Configuration Register | --- | FLAGS
7195 | 28 | 27 | ALARM 13 - Second Configuration Register | --- | FLAGS
7196 | 28 | 28 | ALARM 14 - First Configuration Register | --- | FLAGS
7197 | 28 | 29 | ALARM 14 - Second Configuration Register | --- | FLAGS
7198 | 28 | 30 | ALARM 15 - First Configuration Register | --- | FLAGS
7199 | 28 | 31 | ALARM 15 - Second Configuration Register | --- | FLAGS
7200 | 28 | 32 | ALARM 16 - First Configuration Register | --- | FLAGS
7201 | 28 | 33 | ALARM 16 - Second Configuration Register | --- | FLAGS
7202 | 28 | 34 | ALARM 17 - First Configuration Register | --- | FLAGS
7203 | 28 | 35 | ALARM 17 - Second Configuration Register | --- | FLAGS
7204 | 28 | 36 | ALARM 18 - First Configuration Register | --- | FLAGS
7205 | 28 | 37 | ALARM 18 - Second Configuration Register | --- | FLAGS
7206 | 28 | 38 | ALARM 19 - First Configuration Register | --- | FLAGS
7207 | 28 | 39 | ALARM 19 - Second Configuration Register | --- | FLAGS
7208 | 28 | 40 | ALARM 20 - First Configuration Register | --- | FLAGS
7209 | 28 | 41 | ALARM 20 - Second Configuration Register | --- | FLAGS
7210 | 28 | 42 | ALARM 21 - First Configuration Register | --- | FLAGS
7211 | 28 | 43 | ALARM 21 - Second Configuration Register | --- | FLAGS
7212 | 28 | 44 | ALARM 22 - First Configuration Register | --- | FLAGS
7213 | 28 | 45 | ALARM 22 - Second Configuration Register | --- | FLAGS
7214 | 28 | 46 | ALARM 23 - First Configuration Register | --- | FLAGS
7215 | 28 | 47 | ALARM 23 - Second Configuration Register | --- | FLAGS
7216 | 28 | 48 | ALARM 24 - First Configuration Register | --- | FLAGS
7217 | 28 | 49 | ALARM 24 - Second Configuration Register | --- | FLAGS
7218 | 28 | 50 | ALARM 25 - First Configuration Register | --- | FLAGS
7219 | 28 | 51 | ALARM 25 - Second Configuration Register | --- | FLAGS
7220 | 28 | 52 | ALARM 26 - First Configuration Register | --- | FLAGS
7221 | 28 | 53 | ALARM 26 - Second Configuration Register | --- | FLAGS
7222 | 28 | 54 | ALARM 27 - First Configuration Register | --- | FLAGS
7223 | 28 | 55 | ALARM 27 - Second Configuration Register | --- | FLAGS
7224 | 28 | 56 | ALARM 28 - First Configuration Register | --- | FLAGS
7225 | 28 | 57 | ALARM 28 - Second Configuration Register | --- | FLAGS
7226 | 28 | 58 | ALARM 29 - First Configuration Register | --- | FLAGS
7227 | 28 | 59 | ALARM 29 - Second Configuration Register | --- | FLAGS
7228 | 28 | 60 | ALARM 30 - First Configuration Register | --- | FLAGS
7229 | 28 | 61 | ALARM 30 - Second Configuration Register | --- | FLAGS
7230 | 28 | 62 | ALARM 31 - First Configuration Register | --- | FLAGS
7231 | 28 | 63 | ALARM 31 - Second Configuration Register | --- | FLAGS
7232 | 28 | 64 | ALARM 32 - First Configuration Register | --- | FLAGS
7233 | 28 | 65 | ALARM 32 - Second Configuration Register | --- | FLAGS
7234 | 28 | 66 | ALARM 33 - First Configuration Register | --- | FLAGS
7235 | 28 | 67 | ALARM 33 - Second Configuration Register | --- | FLAGS
7236 | 28 | 68 | ALARM 34 - First Configuration Register | --- | FLAGS
7237 | 28 | 69 | ALARM 34 - Second Configuration Register | --- | FLAGS
7238 | 28 | 70 | ALARM 35 - First Configuration Register | --- | FLAGS
7239 | 28 | 71 | ALARM 35 - Second Configuration Register | --- | FLAGS
7240 | 28 | 72 | ALARM 36 - First Configuration Register | --- | FLAGS
7241 | 28 | 73 | ALARM 36 - Second Configuration Register | --- | FLAGS
7242 | 28 | 74 | ALARM 37 - First Configuration Register | --- | FLAGS
7243 | 28 | 75 | ALARM 37 - Second Configuration Register | --- | FLAGS
7244 | 28 | 76 | ALARM 38 - First Configuration Register | --- | FLAGS
7245 | 28 | 77 | ALARM 38 - Second Configuration Register | --- | FLAGS
7246 | 28 | 78 | ALARM 39 - First Configuration Register | --- | FLAGS
7247 | 28 | 79 | ALARM 39 - Second Configuration Register | --- | FLAGS
7248 | 28 | 80 | ALARM 40 - First Configuration Register | --- | FLAGS
7249 | 28 | 81 | ALARM 40 - Second Configuration Register | --- | FLAGS
7250 | 28 | 82 | ALARM 41 - First Configuration Register | --- | FLAGS
7251 | 28 | 83 | ALARM 41 - Second Configuration Register | --- | FLAGS
7252 | 28 | 84 | ALARM 42 - First Configuration Register | --- | FLAGS
7253 | 28 | 85 | ALARM 42 - Second Configuration Register | --- | FLAGS
7254 | 28 | 86 | ALARM 43 - First Configuration Register | --- | FLAGS
7255 | 28 | 87 | ALARM 43 - Second Configuration Register | --- | FLAGS
7256 | 28 | 88 | ALARM 44 - First Configuration Register | --- | FLAGS
7257 | 28 | 89 | ALARM 44 - Second Configuration Register | --- | FLAGS
7258 | 28 | 90 | ALARM 45 - First Configuration Register | --- | FLAGS
7259 | 28 | 91 | ALARM 45 - Second Configuration Register | --- | FLAGS
7260 | 28 | 92 | ALARM 46 - First Configuration Register | --- | FLAGS
7261 | 28 | 93 | ALARM 46 - Second Configuration Register | --- | FLAGS
7262 | 28 | 94 | ALARM 47 - First Configuration Register | --- | FLAGS
7263 | 28 | 95 | ALARM 47 - Second Configuration Register | --- | FLAGS
7264 | 28 | 96 | ALARM 48 - First Configuration Register | --- | FLAGS
7265 | 28 | 97 | ALARM 48 - Second Configuration Register | --- | FLAGS
7266 | 28 | 98 | ALARM 49 - First Configuration Register | --- | FLAGS
7267 | 28 | 99 | ALARM 49 - Second Configuration Register | --- | FLAGS
7268 | 28 | 100 | ALARM 50 - First Configuration Register | --- | FLAGS
7269 | 28 | 101 | ALARM 50 - Second Configuration Register | --- | FLAGS
7270 | 28 | 102 | ALARM 51 - First Configuration Register | --- | FLAGS
7271 | 28 | 103 | ALARM 51 - Second Configuration Register | --- | FLAGS
7272 | 28 | 104 | ALARM 52 - First Configuration Register | --- | FLAGS
7273 | 28 | 105 | ALARM 52 - Second Configuration Register | --- | FLAGS
7274 | 28 | 106 | ALARM 53 - First Configuration Register | --- | FLAGS
7275 | 28 | 107 | ALARM 53 - Second Configuration Register | --- | FLAGS
7276 | 28 | 108 | ALARM 54 - First Configuration Register | --- | FLAGS
7277 | 28 | 109 | ALARM 54 - Second Configuration Register | --- | FLAGS
7278 | 28 | 110 | ALARM 55 - First Configuration Register | --- | FLAGS
7279 | 28 | 111 | ALARM 55 - Second Configuration Register | --- | FLAGS
7280 | 28 | 112 | ALARM 56 - First Configuration Register | --- | FLAGS
7281 | 28 | 113 | ALARM 56 - Second Configuration Register | --- | FLAGS
7282 | 28 | 114 | ALARM 57 - First Configuration Register | --- | FLAGS
7283 | 28 | 115 | ALARM 57 - Second Configuration Register | --- | FLAGS
7284 | 28 | 116 | ALARM 58 - First Configuration Register | --- | FLAGS
7285 | 28 | 117 | ALARM 58 - Second Configuration Register | --- | FLAGS
7286 | 28 | 118 | ALARM 59 - First Configuration Register | --- | FLAGS
7287 | 28 | 119 | ALARM 59 - Second Configuration Register | --- | FLAGS
7288 | 28 | 120 | ALARM 60 - First Configuration Register | --- | FLAGS
7289 | 28 | 121 | ALARM 60 - Second Configuration Register | --- | FLAGS
7290 | 28 | 122 | ALARM 61 - First Configuration Register | --- | FLAGS
7291 | 28 | 123 | ALARM 61 - Second Configuration Register | --- | FLAGS
7292 | 28 | 124 | ALARM 62 - First Configuration Register | --- | FLAGS
7293 | 28 | 125 | ALARM 62 - Second Configuration Register | --- | FLAGS
7294 | 28 | 126 | ALARM 63 - First Configuration Register | --- | FLAGS
7295 | 28 | 127 | ALARM 63 - Second Configuration Register | --- | FLAGS
7296 | 28 | 128 | ALARM 64 - First Configuration Register | --- | FLAGS
7297 | 28 | 129 | ALARM 64 - Second Configuration Register | --- | FLAGS
7298 | 28 | 130 | ALARM 65 - First Configuration Register | --- | FLAGS
7299 | 28 | 131 | ALARM 65 - Second Configuration Register | --- | FLAGS
7300 | 28 | 132 | ALARM 66 - First Configuration Register | --- | FLAGS
7301 | 28 | 133 | ALARM 66 - Second Configuration Register | --- | FLAGS
7302 | 28 | 134 | ALARM 67 - First Configuration Register | --- | FLAGS
7303 | 28 | 135 | ALARM 67 - Second Configuration Register | --- | FLAGS
7304 | 28 | 136 | ALARM 68 - First Configuration Register | --- | FLAGS
7305 | 28 | 137 | ALARM 68 - Second Configuration Register | --- | FLAGS
7306 | 28 | 138 | ALARM 69 - First Configuration Register | --- | FLAGS
7307 | 28 | 139 | ALARM 69 - Second Configuration Register | --- | FLAGS
7308 | 28 | 140 | ALARM 70 - First Configuration Register | --- | FLAGS
7309 | 28 | 141 | ALARM 70 - Second Configuration Register | --- | FLAGS
7310 | 28 | 142 | ALARM 71 - First Configuration Register | --- | FLAGS
7311 | 28 | 143 | ALARM 71 - Second Configuration Register | --- | FLAGS
7312 | 28 | 144 | ALARM 72 - First Configuration Register | --- | FLAGS
7313 | 28 | 145 | ALARM 72 - Second Configuration Register | --- | FLAGS
7314 | 28 | 146 | ALARM 73 - First Configuration Register | --- | FLAGS
7315 | 28 | 147 | ALARM 73 - Second Configuration Register | --- | FLAGS
7316 | 28 | 148 | ALARM 74 - First Configuration Register | --- | FLAGS
7317 | 28 | 149 | ALARM 74 - Second Configuration Register | --- | FLAGS
7318 | 28 | 150 | ALARM 75 - First Configuration Register | --- | FLAGS
7319 | 28 | 151 | ALARM 75 - Second Configuration Register | --- | FLAGS
7320 | 28 | 152 | ALARM 76 - First Configuration Register | --- | FLAGS
7321 | 28 | 153 | ALARM 76 - Second Configuration Register | --- | FLAGS
7322 | 28 | 154 | ALARM 77 - First Configuration Register | --- | FLAGS
7323 | 28 | 155 | ALARM 77 - Second Configuration Register | --- | FLAGS
7324 | 28 | 156 | ALARM 78 - First Configuration Register | --- | FLAGS
7325 | 28 | 157 | ALARM 78 - Second Configuration Register | --- | FLAGS
7326 | 28 | 158 | ALARM 79 - First Configuration Register | --- | FLAGS
7327 | 28 | 159 | ALARM 79 - Second Configuration Register | --- | FLAGS
7328 | 28 | 160 | ALARM 80 - First Configuration Register | --- | FLAGS
7329 | 28 | 161 | ALARM 80 - Second Configuration Register | --- | FLAGS
7330 | 28 | 162 | ALARM 81 - First Configuration Register | --- | FLAGS
7331 | 28 | 163 | ALARM 81 - Second Configuration Register | --- | FLAGS
7332 | 28 | 164 | ALARM 82 - First Configuration Register | --- | FLAGS
7333 | 28 | 165 | ALARM 82 - Second Configuration Register | --- | FLAGS
7334 | 28 | 166 | ALARM 83 - First Configuration Register | --- | FLAGS
7335 | 28 | 167 | ALARM 83 - Second Configuration Register | --- | FLAGS
7336 | 28 | 168 | ALARM 84 - First Configuration Register | --- | FLAGS
7337 | 28 | 169 | ALARM 84 - Second Configuration Register | --- | FLAGS
7338 | 28 | 170 | ALARM 85 - First Configuration Register | --- | FLAGS
7339 | 28 | 171 | ALARM 85 - Second Configuration Register | --- | FLAGS
7340 | 28 | 172 | ALARM 86 - First Configuration Register | --- | FLAGS
7341 | 28 | 173 | ALARM 86 - Second Configuration Register | --- | FLAGS
7342 | 28 | 174 | ALARM 87 - First Configuration Register | --- | FLAGS
7343 | 28 | 175 | ALARM 87 - Second Configuration Register | --- | FLAGS
7344 | 28 | 176 | ALARM 88 - First Configuration Register | --- | FLAGS
7345 | 28 | 177 | ALARM 88 - Second Configuration Register | --- | FLAGS
7346 | 28 | 178 | ALARM 89 - First Configuration Register | --- | FLAGS
7347 | 28 | 179 | ALARM 89 - Second Configuration Register | --- | FLAGS
7348 | 28 | 180 | ALARM 90 - First Configuration Register | --- | FLAGS
7349 | 28 | 181 | ALARM 90 - Second Configuration Register | --- | FLAGS
7350 | 28 | 182 | ALARM 91 - First Configuration Register | --- | FLAGS
7351 | 28 | 183 | ALARM 91 - Second Configuration Register | --- | FLAGS
7352 | 28 | 184 | ALARM 92 - First Configuration Register | --- | FLAGS
7353 | 28 | 185 | ALARM 92 - Second Configuration Register | --- | FLAGS
7354 | 28 | 186 | ALARM 93 - First Configuration Register | --- | FLAGS
7355 | 28 | 187 | ALARM 93 - Second Configuration Register | --- | FLAGS
7356 | 28 | 188 | ALARM 94 - First Configuration Register | --- | FLAGS
7357 | 28 | 189 | ALARM 94 - Second Configuration Register | --- | FLAGS
7358 | 28 | 190 | ALARM 95 - First Configuration Register | --- | FLAGS
7359 | 28 | 191 | ALARM 95 - Second Configuration Register | --- | FLAGS
7360 | 28 | 192 | ALARM 96 - First Configuration Register | --- | FLAGS
7361 | 28 | 193 | ALARM 96 - Second Configuration Register | --- | FLAGS
7362 | 28 | 194 | ALARM 97 - First Configuration Register | --- | FLAGS
7363 | 28 | 195 | ALARM 97 - Second Configuration Register | --- | FLAGS
7364 | 28 | 196 | ALARM 98 - First Configuration Register | --- | FLAGS
7365 | 28 | 197 | ALARM 98 - Second Configuration Register | --- | FLAGS
7366 | 28 | 198 | ALARM 99 - First Configuration Register | --- | FLAGS
7367 | 28 | 199 | ALARM 99 - Second Configuration Register | --- | FLAGS
7368 | 28 | 200 | ALARM 100 - First Configuration Register | --- | FLAGS
7369 | 28 | 201 | ALARM 100 - Second Configuration Register | --- | FLAGS
7370 | 28 | 202 | ALARM 101 - First Configuration Register | --- | FLAGS
7371 | 28 | 203 | ALARM 101 - Second Configuration Register | --- | FLAGS
7372 | 28 | 204 | ALARM 102 - First Configuration Register | --- | FLAGS
7373 | 28 | 205 | ALARM 102 - Second Configuration Register | --- | FLAGS
7374 | 28 | 206 | ALARM 103 - First Configuration Register | --- | FLAGS
7375 | 28 | 207 | ALARM 103 - Second Configuration Register | --- | FLAGS
7376 | 28 | 208 | ALARM 104 - First Configuration Register | --- | FLAGS
7377 | 28 | 209 | ALARM 104 - Second Configuration Register | --- | FLAGS
7378 | 28 | 210 | ALARM 105 - First Configuration Register | --- | FLAGS
7379 | 28 | 211 | ALARM 105 - Second Configuration Register | --- | FLAGS
7380 | 28 | 212 | ALARM 106 - First Configuration Register | --- | FLAGS
7381 | 28 | 213 | ALARM 106 - Second Configuration Register | --- | FLAGS
7382 | 28 | 214 | ALARM 107 - First Configuration Register | --- | FLAGS
7383 | 28 | 215 | ALARM 107 - Second Configuration Register | --- | FLAGS
7384 | 28 | 216 | ALARM 108 - First Configuration Register | --- | FLAGS
7385 | 28 | 217 | ALARM 108 - Second Configuration Register | --- | FLAGS
7386 | 28 | 218 | ALARM 109 - First Configuration Register | --- | FLAGS
7387 | 28 | 219 | ALARM 109 - Second Configuration Register | --- | FLAGS
7388 | 28 | 220 | ALARM 110 - First Configuration Register | --- | FLAGS
7389 | 28 | 221 | ALARM 110 - Second Configuration Register | --- | FLAGS
7390 | 28 | 222 | ALARM 111 - First Configuration Register | --- | FLAGS
7391 | 28 | 223 | ALARM 111 - Second Configuration Register | --- | FLAGS
7392 | 28 | 224 | ALARM 112 - First Configuration Register | --- | FLAGS
7393 | 28 | 225 | ALARM 112 - Second Configuration Register | --- | FLAGS
7394 | 28 | 226 | ALARM 113 - First Configuration Register | --- | FLAGS
7395 | 28 | 227 | ALARM 113 - Second Configuration Register | --- | FLAGS
7396 | 28 | 228 | ALARM 114 - First Configuration Register | --- | FLAGS
7397 | 28 | 229 | ALARM 114 - Second Configuration Register | --- | FLAGS
7398 | 28 | 230 | ALARM 115 - First Configuration Register | --- | FLAGS
7399 | 28 | 231 | ALARM 115 - Second Configuration Register | --- | FLAGS
7400 | 28 | 232 | ALARM 116 - First Configuration Register | --- | FLAGS
7401 | 28 | 233 | ALARM 116 - Second Configuration Register | --- | FLAGS
7402 | 28 | 234 | ALARM 117 - First Configuration Register | --- | FLAGS
7403 | 28 | 235 | ALARM 117 - Second Configuration Register | --- | FLAGS
7404 | 28 | 236 | ALARM 118 - First Configuration Register | --- | FLAGS
7405 | 28 | 237 | ALARM 118 - Second Configuration Register | --- | FLAGS
7406 | 28 | 238 | ALARM 119 - First Configuration Register | --- | FLAGS
7407 | 28 | 239 | ALARM 119 - Second Configuration Register | --- | FLAGS
7408 | 28 | 240 | ALARM 120 - First Configuration Register | --- | FLAGS
7409 | 28 | 241 | ALARM 120 - Second Configuration Register | --- | FLAGS
7410 | 28 | 242 | ALARM 121 - First Configuration Register | --- | FLAGS
7411 | 28 | 243 | ALARM 121 - Second Configuration Register | --- | FLAGS
7412 | 28 | 244 | ALARM 122 - First Configuration Register | --- | FLAGS
7413 | 28 | 245 | ALARM 122 - Second Configuration Register | --- | FLAGS
7414 | 28 | 246 | ALARM 123 - First Configuration Register | --- | FLAGS
7415 | 28 | 247 | ALARM 123 - Second Configuration Register | --- | FLAGS
7416 | 28 | 248 | ALARM 124 - First Configuration Register | --- | FLAGS
7417 | 28 | 249 | ALARM 124 - Second Configuration Register | --- | FLAGS
7418 | 28 | 250 | ALARM 125 - First Configuration Register | --- | FLAGS
7419 | 28 | 251 | ALARM 125 - Second Configuration Register | --- | FLAGS
7420 | 28 | 252 | ALARM 126 - First Configuration Register | --- | FLAGS
7421 | 28 | 253 | ALARM 126 - Second Configuration Register | --- | FLAGS
7422 | 28 | 254 | ALARM 127 - First Configuration Register | --- | FLAGS
7423 | 28 | 255 | ALARM 127 - Second Configuration Register | --- | FLAGS
7424 | 29 | 0 | ALARM 128 - First Configuration Register | --- | FLAGS
7425 | 29 | 1 | ALARM 128 - Second Configuration Register | --- | FLAGS
7426 | 29 | 2 | ALARM 129 - First Configuration Register | --- | FLAGS
7427 | 29 | 3 | ALARM 129 - Second Configuration Register | --- | FLAGS
7428 | 29 | 4 | ALARM 130 - First Configuration Register | --- | FLAGS
7429 | 29 | 5 | ALARM 130 - Second Configuration Register | --- | FLAGS
7430 | 29 | 6 | ALARM 131 - First Configuration Register | --- | FLAGS
7431 | 29 | 7 | ALARM 131 - Second Configuration Register | --- | FLAGS
7432 | 29 | 8 | ALARM 132 - First Configuration Register | --- | FLAGS
7433 | 29 | 9 | ALARM 132 - Second Configuration Register | --- | FLAGS
7434 | 29 | 10 | ALARM 133 - First Configuration Register | --- | FLAGS
7435 | 29 | 11 | ALARM 133 - Second Configuration Register | --- | FLAGS
7436 | 29 | 12 | ALARM 134 - First Configuration Register | --- | FLAGS
7437 | 29 | 13 | ALARM 134 - Second Configuration Register | --- | FLAGS
7438 | 29 | 14 | ALARM 135 - First Configuration Register | --- | FLAGS
7439 | 29 | 15 | ALARM 135 - Second Configuration Register | --- | FLAGS
7440 | 29 | 16 | ALARM 136 - First Configuration Register | --- | FLAGS
7441 | 29 | 17 | ALARM 136 - Second Configuration Register | --- | FLAGS
7442 | 29 | 18 | ALARM 137 - First Configuration Register | --- | FLAGS
7443 | 29 | 19 | ALARM 137 - Second Configuration Register | --- | FLAGS
7444 | 29 | 20 | ALARM 138 - First Configuration Register | --- | FLAGS
7445 | 29 | 21 | ALARM 138 - Second Configuration Register | --- | FLAGS
7446 | 29 | 22 | ALARM 139 - First Configuration Register | --- | FLAGS
7447 | 29 | 23 | ALARM 139 - Second Configuration Register | --- | FLAGS
7448 | 29 | 24 | ALARM 140 - First Configuration Register | --- | FLAGS
7449 | 29 | 25 | ALARM 140 - Second Configuration Register | --- | FLAGS
7450 | 29 | 26 | ALARM 141 - First Configuration Register | --- | FLAGS
7451 | 29 | 27 | ALARM 141 - Second Configuration Register | --- | FLAGS
7452 | 29 | 28 | ALARM 142 - First Configuration Register | --- | FLAGS
7453 | 29 | 29 | ALARM 142 - Second Configuration Register | --- | FLAGS
7454 | 29 | 30 | ALARM 143 - First Configuration Register | --- | FLAGS
7455 | 29 | 31 | ALARM 143 - Second Configuration Register | --- | FLAGS
7456 | 29 | 32 | ALARM 144 - First Configuration Register | --- | FLAGS
7457 | 29 | 33 | ALARM 144 - Second Configuration Register | --- | FLAGS
7458 | 29 | 34 | ALARM 145 - First Configuration Register | --- | FLAGS
7459 | 29 | 35 | ALARM 145 - Second Configuration Register | --- | FLAGS
7460 | 29 | 36 | ALARM 146 - First Configuration Register | --- | FLAGS
7461 | 29 | 37 | ALARM 146 - Second Configuration Register | --- | FLAGS
7462 | 29 | 38 | ALARM 147 - First Configuration Register | --- | FLAGS
7463 | 29 | 39 | ALARM 147 - Second Configuration Register | --- | FLAGS
7464 | 29 | 40 | ALARM 148 - First Configuration Register | --- | FLAGS
7465 | 29 | 41 | ALARM 148 - Second Configuration Register | --- | FLAGS
7466 | 29 | 42 | ALARM 149 - First Configuration Register | --- | FLAGS
7467 | 29 | 43 | ALARM 149 - Second Configuration Register | --- | FLAGS
7468 | 29 | 44 | ALARM 150 - First Configuration Register | --- | FLAGS
7469 | 29 | 45 | ALARM 150 - Second Configuration Register | --- | FLAGS
7470 | 29 | 46 | ALARM 151 - First Configuration Register | --- | FLAGS
7471 | 29 | 47 | ALARM 151 - Second Configuration Register | --- | FLAGS
7472 | 29 | 48 | ALARM 152 - First Configuration Register | --- | FLAGS
7473 | 29 | 49 | ALARM 152 - Second Configuration Register | --- | FLAGS
7474 | 29 | 50 | ALARM 153 - First Configuration Register | --- | FLAGS
7475 | 29 | 51 | ALARM 153 - Second Configuration Register | --- | FLAGS
7476 | 29 | 52 | ALARM 154 - First Configuration Register | --- | FLAGS
7477 | 29 | 53 | ALARM 154 - Second Configuration Register | --- | FLAGS
7478 | 29 | 54 | ALARM 155 - First Configuration Register | --- | FLAGS
7479 | 29 | 55 | ALARM 155 - Second Configuration Register | --- | FLAGS
7480 | 29 | 56 | ALARM 156 - First Configuration Register | --- | FLAGS
7481 | 29 | 57 | ALARM 156 - Second Configuration Register | --- | FLAGS
7482 | 29 | 58 | ALARM 157 - First Configuration Register | --- | FLAGS
7483 | 29 | 59 | ALARM 157 - Second Configuration Register | --- | FLAGS
7484 | 29 | 60 | ALARM 158 - First Configuration Register | --- | FLAGS
7485 | 29 | 61 | ALARM 158 - Second Configuration Register | --- | FLAGS
7486 | 29 | 62 | ALARM 159 - First Configuration Register | --- | FLAGS
7487 | 29 | 63 | ALARM 159 - Second Configuration Register | --- | FLAGS
7488 | 29 | 64 | ALARM 160 - First Configuration Register | --- | FLAGS
7489 | 29 | 65 | ALARM 160 - Second Configuration Register | --- | FLAGS
7490 | 29 | 66 | ALARM 161 - First Configuration Register | --- | FLAGS
7491 | 29 | 67 | ALARM 161 - Second Configuration Register | --- | FLAGS
7492 | 29 | 68 | ALARM 162 - First Configuration Register | --- | FLAGS
7493 | 29 | 69 | ALARM 162 - Second Configuration Register | --- | FLAGS
7494 | 29 | 70 | ALARM 163 - First Configuration Register | --- | FLAGS
7495 | 29 | 71 | ALARM 163 - Second Configuration Register | --- | FLAGS
7496 | 29 | 72 | ALARM 164 - First Configuration Register | --- | FLAGS
7497 | 29 | 73 | ALARM 164 - Second Configuration Register | --- | FLAGS
7498 | 29 | 74 | ALARM 165 - First Configuration Register | --- | FLAGS
7499 | 29 | 75 | ALARM 165 - Second Configuration Register | --- | FLAGS
7500 | 29 | 76 | ALARM 166 - First Configuration Register | --- | FLAGS
7501 | 29 | 77 | ALARM 166 - Second Configuration Register | --- | FLAGS
7502 | 29 | 78 | ALARM 167 - First Configuration Register | --- | FLAGS
7503 | 29 | 79 | ALARM 167 - Second Configuration Register | --- | FLAGS
7504 | 29 | 80 | ALARM 168 - First Configuration Register | --- | FLAGS
7505 | 29 | 81 | ALARM 168 - Second Configuration Register | --- | FLAGS
7506 | 29 | 82 | ALARM 169 - First Configuration Register | --- | FLAGS
7507 | 29 | 83 | ALARM 169 - Second Configuration Register | --- | FLAGS
7508 | 29 | 84 | ALARM 170 - First Configuration Register | --- | FLAGS
7509 | 29 | 85 | ALARM 170 - Second Configuration Register | --- | FLAGS
7510 | 29 | 86 | ALARM 171 - First Configuration Register | --- | FLAGS
7511 | 29 | 87 | ALARM 171 - Second Configuration Register | --- | FLAGS
7512 | 29 | 88 | ALARM 172 - First Configuration Register | --- | FLAGS
7513 | 29 | 89 | ALARM 172 - Second Configuration Register | --- | FLAGS
7514 | 29 | 90 | ALARM 173 - First Configuration Register | --- | FLAGS
7515 | 29 | 91 | ALARM 173 - Second Configuration Register | --- | FLAGS
7516 | 29 | 92 | ALARM 174 - First Configuration Register | --- | FLAGS
7517 | 29 | 93 | ALARM 174 - Second Configuration Register | --- | FLAGS
7518 | 29 | 94 | ALARM 175 - First Configuration Register | --- | FLAGS
7519 | 29 | 95 | ALARM 175 - Second Configuration Register | --- | FLAGS
7520 | 29 | 96 | ALARM 176 - First Configuration Register | --- | FLAGS
7521 | 29 | 97 | ALARM 176 - Second Configuration Register | --- | FLAGS
7522 | 29 | 98 | ALARM 177 - First Configuration Register | --- | FLAGS
7523 | 29 | 99 | ALARM 177 - Second Configuration Register | --- | FLAGS
7524 | 29 | 100 | ALARM 178 - First Configuration Register | --- | FLAGS
7525 | 29 | 101 | ALARM 178 - Second Configuration Register | --- | FLAGS
7526 | 29 | 102 | ALARM 179 - First Configuration Register | --- | FLAGS
7527 | 29 | 103 | ALARM 179 - Second Configuration Register | --- | FLAGS
7528 | 29 | 104 | ALARM 180 - First Configuration Register | --- | FLAGS
7529 | 29 | 105 | ALARM 180 - Second Configuration Register | --- | FLAGS
7530 | 29 | 106 | ALARM 181 - First Configuration Register | --- | FLAGS
7531 | 29 | 107 | ALARM 181 - Second Configuration Register | --- | FLAGS
7532 | 29 | 108 | ALARM 182 - First Configuration Register | --- | FLAGS
7533 | 29 | 109 | ALARM 182 - Second Configuration Register | --- | FLAGS
7534 | 29 | 110 | ALARM 183 - First Configuration Register | --- | FLAGS
7535 | 29 | 111 | ALARM 183 - Second Configuration Register | --- | FLAGS
7536 | 29 | 112 | ALARM 184 - First Configuration Register | --- | FLAGS
7537 | 29 | 113 | ALARM 184 - Second Configuration Register | --- | FLAGS
7538 | 29 | 114 | ALARM 185 - First Configuration Register | --- | FLAGS
7539 | 29 | 115 | ALARM 185 - Second Configuration Register | --- | FLAGS
7540 | 29 | 116 | ALARM 186 - First Configuration Register | --- | FLAGS
7541 | 29 | 117 | ALARM 186 - Second Configuration Register | --- | FLAGS
7542 | 29 | 118 | ALARM 187 - First Configuration Register | --- | FLAGS
7543 | 29 | 119 | ALARM 187 - Second Configuration Register | --- | FLAGS
7544 | 29 | 120 | ALARM 188 - First Configuration Register | --- | FLAGS
7545 | 29 | 121 | ALARM 188 - Second Configuration Register | --- | FLAGS
7546 | 29 | 122 | ALARM 189 - First Configuration Register | --- | FLAGS
7547 | 29 | 123 | ALARM 189 - Second Configuration Register | --- | FLAGS
7548 | 29 | 124 | ALARM 190 - First Configuration Register | --- | FLAGS
7549 | 29 | 125 | ALARM 190 - Second Configuration Register | --- | FLAGS
7550 | 29 | 126 | ALARM 191 - First Configuration Register | --- | FLAGS
7551 | 29 | 127 | ALARM 191 - Second Configuration Register | --- | FLAGS
7552 | 29 | 128 | ALARM 192 - First Configuration Register | --- | FLAGS
7553 | 29 | 129 | ALARM 192 - Second Configuration Register | --- | FLAGS
7554 | 29 | 130 | ALARM 193 - First Configuration Register | --- | FLAGS
7555 | 29 | 131 | ALARM 193 - Second Configuration Register | --- | FLAGS
7556 | 29 | 132 | ALARM 194 - First Configuration Register | --- | FLAGS
7557 | 29 | 133 | ALARM 194 - Second Configuration Register | --- | FLAGS
7558 | 29 | 134 | ALARM 195 - First Configuration Register | --- | FLAGS
7559 | 29 | 135 | ALARM 195 - Second Configuration Register | --- | FLAGS
7560 | 29 | 136 | ALARM 196 - First Configuration Register | --- | FLAGS
7561 | 29 | 137 | ALARM 196 - Second Configuration Register | --- | FLAGS
7562 | 29 | 138 | ALARM 197 - First Configuration Register | --- | FLAGS
7563 | 29 | 139 | ALARM 197 - Second Configuration Register | --- | FLAGS
7564 | 29 | 140 | ALARM 198 - First Configuration Register | --- | FLAGS
7565 | 29 | 141 | ALARM 198 - Second Configuration Register | --- | FLAGS
7566 | 29 | 142 | ALARM 199 - First Configuration Register | --- | FLAGS
7567 | 29 | 143 | ALARM 199 - Second Configuration Register | --- | FLAGS
7568 | 29 | 144 | ALARM 200 - First Configuration Register | --- | FLAGS
7569 | 29 | 145 | ALARM 200 - Second Configuration Register | --- | FLAGS
7570 | 29 | 146 | ALARM 201 - First Configuration Register | --- | FLAGS
7571 | 29 | 147 | ALARM 201 - Second Configuration Register | --- | FLAGS
7572 | 29 | 148 | ALARM 202 - First Configuration Register | --- | FLAGS
7573 | 29 | 149 | ALARM 202 - Second Configuration Register | --- | FLAGS
7574 | 29 | 150 | ALARM 203 - First Configuration Register | --- | FLAGS
7575 | 29 | 151 | ALARM 203 - Second Configuration Register | --- | FLAGS
7576 | 29 | 152 | ALARM 204 - First Configuration Register | --- | FLAGS
7577 | 29 | 153 | ALARM 204 - Second Configuration Register | --- | FLAGS
7578 | 29 | 154 | ALARM 205 - First Configuration Register | --- | FLAGS
7579 | 29 | 155 | ALARM 205 - Second Configuration Register | --- | FLAGS
7580 | 29 | 156 | ALARM 206 - First Configuration Register | --- | FLAGS
7581 | 29 | 157 | ALARM 206 - Second Configuration Register | --- | FLAGS
7582 | 29 | 158 | ALARM 207 - First Configuration Register | --- | FLAGS
7583 | 29 | 159 | ALARM 207 - Second Configuration Register | --- | FLAGS
7584 | 29 | 160 | ALARM 208 - First Configuration Register | --- | FLAGS
7585 | 29 | 161 | ALARM 208 - Second Configuration Register | --- | FLAGS
7586 | 29 | 162 | ALARM 209 - First Configuration Register | --- | FLAGS
7587 | 29 | 163 | ALARM 209 - Second Configuration Register | --- | FLAGS
7588 | 29 | 164 | ALARM 210 - First Configuration Register | --- | FLAGS
7589 | 29 | 165 | ALARM 210 - Second Configuration Register | --- | FLAGS
7590 | 29 | 166 | ALARM 211 - First Configuration Register | --- | FLAGS
7591 | 29 | 167 | ALARM 211 - Second Configuration Register | --- | FLAGS
7592 | 29 | 168 | ALARM 212 - First Configuration Register | --- | FLAGS
7593 | 29 | 169 | ALARM 212 - Second Configuration Register | --- | FLAGS
7594 | 29 | 170 | ALARM 213 - First Configuration Register | --- | FLAGS
7595 | 29 | 171 | ALARM 213 - Second Configuration Register | --- | FLAGS
7596 | 29 | 172 | ALARM 214 - First Configuration Register | --- | FLAGS
7597 | 29 | 173 | ALARM 214 - Second Configuration Register | --- | FLAGS
7598 | 29 | 174 | ALARM 215 - First Configuration Register | --- | FLAGS
7599 | 29 | 175 | ALARM 215 - Second Configuration Register | --- | FLAGS
7600 | 29 | 176 | ALARM 216 - First Configuration Register | --- | FLAGS
7601 | 29 | 177 | ALARM 216 - Second Configuration Register | --- | FLAGS
7602 | 29 | 178 | ALARM 217 - First Configuration Register | --- | FLAGS
7603 | 29 | 179 | ALARM 217 - Second Configuration Register | --- | FLAGS
7604 | 29 | 180 | ALARM 218 - First Configuration Register | --- | FLAGS
7605 | 29 | 181 | ALARM 218 - Second Configuration Register | --- | FLAGS
7606 | 29 | 182 | ALARM 219 - First Configuration Register | --- | FLAGS
7607 | 29 | 183 | ALARM 219 - Second Configuration Register | --- | FLAGS
7608 | 29 | 184 | ALARM 220 - First Configuration Register | --- | FLAGS
7609 | 29 | 185 | ALARM 220 - Second Configuration Register | --- | FLAGS
7610 | 29 | 186 | ALARM 221 - First Configuration Register | --- | FLAGS
7611 | 29 | 187 | ALARM 221 - Second Configuration Register | --- | FLAGS
7612 | 29 | 188 | ALARM 222 - First Configuration Register | --- | FLAGS
7613 | 29 | 189 | ALARM 222 - Second Configuration Register | --- | FLAGS
7614 | 29 | 190 | ALARM 223 - First Configuration Register | --- | FLAGS
7615 | 29 | 191 | ALARM 223 - Second Configuration Register | --- | FLAGS
7616 | 29 | 192 | ALARM 224 - First Configuration Register | --- | FLAGS
7617 | 29 | 193 | ALARM 224 - Second Configuration Register | --- | FLAGS
7618 | 29 | 194 | ALARM 225 - First Configuration Register | --- | FLAGS
7619 | 29 | 195 | ALARM 225 - Second Configuration Register | --- | FLAGS
7620 | 29 | 196 | ALARM 226 - First Configuration Register | --- | FLAGS
7621 | 29 | 197 | ALARM 226 - Second Configuration Register | --- | FLAGS
7622 | 29 | 198 | ALARM 227 - First Configuration Register | --- | FLAGS
7623 | 29 | 199 | ALARM 227 - Second Configuration Register | --- | FLAGS
7624 | 29 | 200 | ALARM 228 - First Configuration Register | --- | FLAGS
7625 | 29 | 201 | ALARM 228 - Second Configuration Register | --- | FLAGS
7626 | 29 | 202 | ALARM 229 - First Configuration Register | --- | FLAGS
7627 | 29 | 203 | ALARM 229 - Second Configuration Register | --- | FLAGS
7628 | 29 | 204 | ALARM 230 - First Configuration Register | --- | FLAGS
7629 | 29 | 205 | ALARM 230 - Second Configuration Register | --- | FLAGS
7630 | 29 | 206 | ALARM 231 - First Configuration Register | --- | FLAGS
7631 | 29 | 207 | ALARM 231 - Second Configuration Register | --- | FLAGS
7632 | 29 | 208 | ALARM 232 - First Configuration Register | --- | FLAGS
7633 | 29 | 209 | ALARM 232 - Second Configuration Register | --- | FLAGS
7634 | 29 | 210 | ALARM 233 - First Configuration Register | --- | FLAGS
7635 | 29 | 211 | ALARM 233 - Second Configuration Register | --- | FLAGS
7636 | 29 | 212 | ALARM 234 - First Configuration Register | --- | FLAGS
7637 | 29 | 213 | ALARM 234 - Second Configuration Register | --- | FLAGS
7638 | 29 | 214 | ALARM 235 - First Configuration Register | --- | FLAGS
7639 | 29 | 215 | ALARM 235 - Second Configuration Register | --- | FLAGS
7640 | 29 | 216 | ALARM 236 - First Configuration Register | --- | FLAGS
7641 | 29 | 217 | ALARM 236 - Second Configuration Register | --- | FLAGS
7642 | 29 | 218 | ALARM 237 - First Configuration Register | --- | FLAGS
7643 | 29 | 219 | ALARM 237 - Second Configuration Register | --- | FLAGS
7644 | 29 | 220 | ALARM 238 - First Configuration Register | --- | FLAGS
7645 | 29 | 221 | ALARM 238 - Second Configuration Register | --- | FLAGS
7646 | 29 | 222 | ALARM 239 - First Configuration Register | --- | FLAGS
7647 | 29 | 223 | ALARM 239 - Second Configuration Register | --- | FLAGS
7648 | 29 | 224 | ALARM 240 - First Configuration Register | --- | FLAGS
7649 | 29 | 225 | ALARM 240 - Second Configuration Register | --- | FLAGS
7650 | 29 | 226 | ALARM 241 - First Configuration Register | --- | FLAGS
7651 | 29 | 227 | ALARM 241 - Second Configuration Register | --- | FLAGS
7652 | 29 | 228 | ALARM 242 - First Configuration Register | --- | FLAGS
7653 | 29 | 229 | ALARM 242 - Second Configuration Register | --- | FLAGS
7654 | 29 | 230 | ALARM 243 - First Configuration Register | --- | FLAGS
7655 | 29 | 231 | ALARM 243 - Second Configuration Register | --- | FLAGS
7656 | 29 | 232 | ALARM 244 - First Configuration Register | --- | FLAGS
7657 | 29 | 233 | ALARM 244 - Second Configuration Register | --- | FLAGS
7658 | 29 | 234 | ALARM 245 - First Configuration Register | --- | FLAGS
7659 | 29 | 235 | ALARM 245 - Second Configuration Register | --- | FLAGS
7660 | 29 | 236 | ALARM 246 - First Configuration Register | --- | FLAGS
7661 | 29 | 237 | ALARM 246 - Second Configuration Register | --- | FLAGS
7662 | 29 | 238 | ALARM 247 - First Configuration Register | --- | FLAGS
7663 | 29 | 239 | ALARM 247 - Second Configuration Register | --- | FLAGS
7664 | 29 | 240 | ALARM 248 - First Configuration Register | --- | FLAGS
7665 | 29 | 241 | ALARM 248 - Second Configuration Register | --- | FLAGS
7666 | 29 | 242 | ALARM 249 - First Configuration Register | --- | FLAGS
7667 | 29 | 243 | ALARM 249 - Second Configuration Register | --- | FLAGS
7668 | 29 | 244 | ALARM 250 - First Configuration Register | --- | FLAGS
7669 | 29 | 245 | ALARM 250 - Second Configuration Register | --- | FLAGS
7670 | 29 | 246 | ALARM 251 - First Configuration Register | --- | FLAGS
7671 | 29 | 247 | ALARM 251 - Second Configuration Register | --- | FLAGS
7672 | 29 | 248 | ALARM 252 - First Configuration Register | --- | FLAGS
7673 | 29 | 249 | ALARM 252 - Second Configuration Register | --- | FLAGS
7674 | 29 | 250 | ALARM 253 - First Configuration Register | --- | FLAGS
7675 | 29 | 251 | ALARM 253 - Second Configuration Register | --- | FLAGS
7676 | 29 | 252 | ALARM 254 - First Configuration Register | --- | FLAGS
7677 | 29 | 253 | ALARM 254 - Second Configuration Register | --- | FLAGS
7678 | 29 | 254 | ALARM 255 - First Configuration Register | --- | FLAGS
7679 | 29 | 255 | ALARM 255 - Second Configuration Register | --- | FLAGS
7680 | 30 | 0 | K Vac (phase R) | --- | FLOAT
7681 | 30 | 1 | Q Vac (phase R) | V | FLOAT
7682 | 30 | 2 | K Vac (phase S) | --- | FLOAT
7683 | 30 | 3 | Q Vac (phase S) | V | FLOAT
7684 | 30 | 4 | K Vac (phase T) | --- | FLOAT
7685 | 30 | 5 | Q Vac (phase T) | V | FLOAT
7686 | 30 | 6 | K Vac (phase Neutral) | --- | FLOAT
7687 | 30 | 7 | Q Vac (phase Neutral) | V | FLOAT
7688 | 30 | 8 | K Iac (phase R) | --- | FLOAT
7689 | 30 | 9 | Q Iac (phase R) | A | FLOAT
7690 | 30 | 10 | K Iac (phase S) | --- | FLOAT
7691 | 30 | 11 | Q Iac (phase S) | A | FLOAT
7692 | 30 | 12 | K Iac (phase T) | --- | FLOAT
7693 | 30 | 13 | Q Iac (phase T) | A | FLOAT
7694 | 30 | 14 | K Vac int (phase R) | --- | FLOAT
7695 | 30 | 15 | Q Vac int (phase R) | V | FLOAT
7696 | 30 | 16 | K Vac int (phase S) | --- | FLOAT
7697 | 30 | 17 | Q Vac int (phase S) | V | FLOAT
7698 | 30 | 18 | K Vac int (phase T) | --- | FLOAT
7699 | 30 | 19 | Q Vac int (phase T) | V | FLOAT
7700 | 30 | 20 | K Vac Backup | --- | FLOAT
7701 | 30 | 21 | Q Vac Backup | V | FLOAT
7702 | 30 | 22 | K Vac (conc RS) | --- | FLOAT
7703 | 30 | 23 | Q Vac (conc RS) | V | FLOAT
7704 | 30 | 24 | K Vac (conc ST) | --- | FLOAT
7705 | 30 | 25 | Q Vac (conc ST) | V | FLOAT
7706 | 30 | 26 | K Vac (conc TR) | --- | FLOAT
7707 | 30 | 27 | Q Vac (conc TR) | V | FLOAT
7708 | 30 | 28 | K Vac split1 | --- | FLOAT
7709 | 30 | 29 | Q Vac split1 | V | FLOAT
7710 | 30 | 30 | K Vac split2 | --- | FLOAT
7711 | 30 | 31 | Q Vac split2 | V | FLOAT
7712 | 30 | 32 | K Vbulk | --- | FLOAT
7713 | 30 | 33 | Q Vbulk | V | FLOAT
7720 | 30 | 40 | K Vin CH1 | --- | FLOAT
7721 | 30 | 41 | Q Vin CH1 | V | FLOAT
7722 | 30 | 42 | K Vin CH2 | --- | FLOAT
7723 | 30 | 43 | Q Vin CH2 | V | FLOAT
7728 | 30 | 48 | K Iin CH1 | --- | FLOAT
7729 | 30 | 49 | Q Iin CH1 | A | FLOAT
7730 | 30 | 50 | K Iin CH2 | --- | FLOAT
7731 | 30 | 51 | Q Iin CH2 | A | FLOAT
7732 | 30 | 52 | K Iin CH3 | --- | FLOAT
7733 | 30 | 53 | Q Iin CH3 | A | FLOAT
7736 | 30 | 56 | K Iin MPPT CH1 | --- | FLOAT
7737 | 30 | 57 | Q Iin MPPT CH1 | V | FLOAT
7738 | 30 | 58 | K Iin MPPT CH2 | --- | FLOAT
7739 | 30 | 59 | Q Iin MPPT CH2 | V | FLOAT
7756 | 30 | 76 | K Vref/2 | --- | FLOAT
7757 | 30 | 77 | Q Vref/2 | V | FLOAT
7808 | 30 | 128 | K Vbattery | --- | FLOAT
7809 | 30 | 129 | Q Vbattery | V | FLOAT
7816 | 30 | 136 | K Ibattery CHARGE | --- | FLOAT
7817 | 30 | 137 | Q Ibattery CHARGE | A | FLOAT
7824 | 30 | 144 | K Ibattery DISCHARGE | --- | FLOAT
7825 | 30 | 145 | Q Ibattery DISCHARGE | A | FLOAT
7840 | 30 | 160 | K Pac R | --- | FLOAT
7841 | 30 | 161 | Q Pac R | W | FLOAT
7842 | 30 | 162 | K Pac S | --- | FLOAT
7843 | 30 | 163 | Q Pac S | W | FLOAT
7844 | 30 | 164 | K Pac T | --- | FLOAT
7845 | 30 | 165 | Q Pac T | W | FLOAT
7846 | 30 | 166 | K Qac R | --- | FLOAT
7847 | 30 | 167 | Q Qac R | VAR | FLOAT
7848 | 30 | 168 | K Qac S | --- | FLOAT
7849 | 30 | 169 | Q Qac S | VAR | FLOAT
7850 | 30 | 170 | K Qac T | --- | FLOAT
7851 | 30 | 171 | Q Qac T | VAR | FLOAT
7852 | 30 | 172 | K Pbatt1 | --- | FLOAT
7853 | 30 | 173 | Q Pbatt1 | W | FLOAT
7854 | 30 | 174 | K Pbatt2 | --- | FLOAT
7855 | 30 | 175 | Q Pbatt2 | W | FLOAT
7856 | 30 | 176 | K Pbatt3 | --- | FLOAT
7857 | 30 | 177 | Q Pbatt3 | W | FLOAT
7858 | 30 | 178 | K Pbatt4 | --- | FLOAT
7859 | 30 | 179 | Q Pbatt4 | W | FLOAT
7860 | 30 | 180 | K COS-PHI | --- | FLOAT
7861 | 30 | 181 | Q COS-PHI | --- | FLOAT
7862 | 30 | 182 | K Vbulk+ | --- | FLOAT
7863 | 30 | 183 | Q Vbulk+ | V | FLOAT
7864 | 30 | 184 | K Vbulk- | --- | FLOAT
7865 | 30 | 185 | Q Vbulk- | V | FLOAT
7866 | 30 | 186 | K V4+ | --- | FLOAT
7867 | 30 | 187 | Q V4+ | V | FLOAT
7868 | 30 | 188 | K V4- | --- | FLOAT
7869 | 30 | 189 | Q V4- | V | FLOAT
7870 | 30 | 190 | K Ipanel | --- | FLOAT
7871 | 30 | 191 | Q Ipanel | A | FLOAT
7884 | 30 | 204 | K DC injection R | --- | FLOAT
7885 | 30 | 205 | Q DC injection R | A | FLOAT
7886 | 30 | 206 | K DC injection S | --- | FLOAT
7887 | 30 | 207 | Q DC injection S | A | FLOAT
7888 | 30 | 208 | K DC injection T | --- | FLOAT
7889 | 30 | 209 | Q DC injection T | A | FLOAT
7890 | 30 | 210 | K Icond (phase R) | --- | FLOAT
7891 | 30 | 211 | Q Icond (phase R) | A | FLOAT
7892 | 30 | 212 | K Icond (phase S) | --- | FLOAT
7893 | 30 | 213 | Q Icond (phase S) | A | FLOAT
7894 | 30 | 214 | K Icond (phase T) | --- | FLOAT
7895 | 30 | 215 | Q Icond (phase T) | A | FLOAT
7896 | 30 | 216 | K Pac Total (fixed reference calculation) | --- | FLOAT
7897 | 30 | 217 | Q Pac Total (fixed reference calculation) | W | FLOAT
7898 | 30 | 218 | K Qac Total (fixed reference calculation) | --- | FLOAT
7899 | 30 | 219 | Q Qac Total (fixed reference calculation) | VAR | FLOAT
7900 | 30 | 220 | K Pin | --- | FLOAT
7901 | 30 | 221 | Q Pin | W | FLOAT
7902 | 30 | 222 | K Active current reference ( ADC slave unit ) | --- | FLOAT
7903 | 30 | 223 | Q Active current reference ( ADC slave unit ) | A | FLOAT
7904 | 30 | 224 | K Active current reference ( master unit ) | --- | FLOAT
7905 | 30 | 225 | Q Active current reference ( master unit ) | A | FLOAT
7906 | 30 | 226 | K positive pole earth voltage | --- | FLOAT
7907 | 30 | 227 | Q positive pole earth voltage | V | FLOAT
7908 | 30 | 228 | K negative pole earth voltage | --- | FLOAT
7909 | 30 | 229 | Q negative pole earth voltage | V | FLOAT
7936 | 31 | 0 | UI display - Culture code | --- | UI8
7937 | 31 | 1 | UI display - 1st level password | --- | STRING
7938 | 31 | 2 | UI display - Contrast level | --- | UI8
7939 | 31 | 3 | UI display - Backlight level | --- | UI8
7940 | 31 | 4 | UI display - Backlight mode | --- | UI8
7941 | 31 | 5 | UI display - Currency Name | --- | STRING
7942 | 31 | 6 | UI display - Cash value | --- | FLOAT
8192 | 32 | 0 | TEST RELAY - CONFIGURATION REGISTER | --- | FLAGS
8193 | 32 | 1 | TEST RELAY - MEASURE DELAY AFTER RELAY CLOSURE | ms | UI32
8194 | 32 | 2 | TEST RELAY - MIN VOLTAGE FOR TEST PASSED | V | FLOAT
8195 | 32 | 3 | TEST RELAY – VERIFICATION TIMEOUT | ms | UI32
8196 | 32 | 4 | TEST RELAY – MIN VOLTAGE VARIATION EXPECTED | V | FLOAT
8224 | 32 | 32 | TEST RELAY - INTERFACE COMPATIBILITY REGISTER | --- | FLAGS
8448 | 33 | 0 | REGULATORS CONFIGURATION REGISTER | --- | FLAGS
8449 | 33 | 1 | KP PLL | --- | FLOAT
8450 | 33 | 2 | KI PLL | --- | FLOAT
8451 | 33 | 3 | PLL Lock Protection | --- | FLOAT
8452 | 33 | 4 | PLL Lock Protection - TOUT | ms | UI32
8453 | 33 | 5 | THETA DELAY | --- | FLOAT
8458 | 33 | 10 | Dominant Current Regulator KP | --- | FLOAT
8459 | 33 | 11 | Dominant Current Regulator KI | --- | FLOAT
8460 | 33 | 12 | Output Dominant Current PI Saturation | A | FLOAT
8461 | 33 | 13 | Recessive Current Regulator KP | --- | FLOAT
8462 | 33 | 14 | Recessive Current Regulator KI | --- | FLOAT
8463 | 33 | 15 | Output Recessive Current PI Saturation | A | FLOAT
8464 | 33 | 16 | Minimum Active Current Saturation | A | FLOAT
8465 | 33 | 17 | ID LOSS CONTROL | A | FLOAT
8466 | 33 | 18 | IQ LOSS CONTROL | A | FLOAT
8467 | 33 | 19 | ID/IQ LOSS CONTROL TOUT | ms | UI32
8478 | 33 | 30 | KP DELTA_BULK | --- | FLOAT
8479 | 33 | 31 | DELTA_BULK OFFSET SATURATION | % | FLOAT
8483 | 33 | 35 | BULK REGULATOR KP | --- | FLOAT
8484 | 33 | 36 | BULK REGULATOR KI | --- | FLOAT
8485 | 33 | 37 | BULK REGULATOR - POSITIVE OUTPUT SATURATION | A | FLOAT
8486 | 33 | 38 | BULK REGULATOR - NEGATIVE OUTPUT SATURATION | A | FLOAT
8490 | 33 | 42 | DAMPING RESISTANCE | Ohm | FLOAT
8491 | 33 | 43 | KP ZERO SEQUENCE | --- | FLOAT
8492 | 33 | 44 | KI ZERO SEQUENCE | --- | FLOAT
8704 | 34 | 0 | SYSTEM UPDATE - CONFIGURATION REGISTER | --- | FLAGS
8960 | 35 | 0 | PWM DISABLE REGISTER | --- | FLAGS
8961 | 35 | 1 | PWM CONTROL 0 - Input measure ID | --- | FLAGS
8962 | 35 | 2 | PWM CONTROL 0 - PWM timer ID | --- | FLAGS
8963 | 35 | 3 | PWM CONTROL 0 - Duty minimum value | --- | FLOAT
8964 | 35 | 4 | PWM CONTROL 0 - Configuration register | --- | FLAGS
8965 | 35 | 5 | PWM CONTROL 1 - Input measure ID | --- | FLAGS
8966 | 35 | 6 | PWM CONTROL 1 - PWM timer ID | --- | FLAGS
8967 | 35 | 7 | PWM CONTROL 1 - Duty minimum value | --- | FLOAT
8968 | 35 | 8 | PWM CONTROL 1 - Configuration register | --- | FLAGS
8969 | 35 | 9 | PWM CONTROL 2 - Input measure ID | --- | FLAGS
8970 | 35 | 10 | PWM CONTROL 2 - PWM timer ID | --- | FLAGS
8971 | 35 | 11 | PWM CONTROL 2 - Duty minimum value | --- | FLOAT
8972 | 35 | 12 | PWM CONTROL 2 - Configuration register | --- | FLAGS
8973 | 35 | 13 | PWM CONTROL 3 - Input measure ID | --- | FLAGS
8974 | 35 | 14 | PWM CONTROL 3 - PWM timer ID | --- | FLAGS
8975 | 35 | 15 | PWM CONTROL 3 - Duty minimum value | --- | FLOAT
8976 | 35 | 16 | PWM CONTROL 3 - Configuration register | --- | FLAGS
9216 | 36 | 0 | DERATING CONTROL 0 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9232 | 36 | 16 | DERATING CONTROL 1 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9248 | 36 | 32 | DERATING CONTROL 2 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9264 | 36 | 48 | DERATING CONTROL 3 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9280 | 36 | 64 | DERATING CONTROL 4 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9296 | 36 | 80 | DERATING CONTROL 5 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9312 | 36 | 96 | DERATING CONTROL 6 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9328 | 36 | 112 | DERATING CONTROL 7 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9344 | 36 | 128 | DERATING CONTROL 8 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9360 | 36 | 144 | DERATING CONTROL 9 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9376 | 36 | 160 | DERATING CONTROL 10 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9392 | 36 | 176 | DERATING CONTROL 11 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9408 | 36 | 192 | DERATING CONTROL 12 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9424 | 36 | 208 | DERATING CONTROL 13 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9440 | 36 | 224 | DERATING CONTROL 14 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9456 | 36 | 240 | DERATING CONTROL 15 EXT. - Control parameter (Val_MAX_Derating / Val_MAX) | --- | FLOAT
9472 | 37 | 0 | CENTRAL MODULE - CONFIGURATION REGISTER | --- | FLAGS
9473 | 37 | 1 | CENTRAL MODULE - MASTER REELECTION TOUT | ms | UI32
9474 | 37 | 2 | CENTRAL MODULE - ALARM COUNTER RESET TOUT | ms | UI32
9475 | 37 | 3 | CENTRAL MODULE - FAN TURN-OFF AFTER FAULT TOUT | ms | UI32
9476 | 37 | 4 | CENTRAL MODULE - FAN FAULT DETECTION TOUT | ms | UI32
9477 | 37 | 5 | CENTRAL MODULE - ENERGY SAVE CLEAR TOUT | ms | UI32
9478 | 37 | 6 | CENTRAL MODULE - T MAX DERATING 1 | °C | FLOAT
9479 | 37 | 7 | CENTRAL MODULE - T MAX DERATING 2 | °C | FLOAT
9480 | 37 | 8 | SYS CONTROLLER STANDBY TOUT | ms | UI32
9728 | 38 | 0 | GOGO RELAY - CONFIGURATION REGISTER | --- | FLAGS
9729 | 38 | 1 | GOGO RELAY - POWER START (P/Pmax) | % | FLOAT
9730 | 38 | 2 | GOGO RELAY - POWER OFF (P/Pstart) | % | FLOAT
9731 | 38 | 3 | GOGO RELAY - MINIMUN TIME RELAY ON | sec | UI32
9732 | 38 | 4 | GOGO RELAY - MINIMUN TIME RELAY OFF | sec | UI32
9984 | 39 | 0 | 3-PH GRID SEQUENCE CONFIGURATION REGISTER | --- | FLAGS
10240 | 40 | 0 | SMOKE SENSOR - CONFIGURATION REGISTER | --- | FLAGS
10241 | 40 | 1 | SMOKE SENSOR - VARIANCE THERSHOLD | --- | FLOAT
10242 | 40 | 2 | SMOKE SENSOR - MAX I Txon THRESHOLD | uA | FLOAT
10243 | 40 | 3 | SMOKE SENSOR - MIN I Txon THRESHOLD | uA | FLOAT
10244 | 40 | 4 | SMOKE SENSOR - MAX I Rxoff THRESHOLD | uA | FLOAT
10245 | 40 | 5 | SMOKE SENSOR - MAX I Txon THRESHOLD CONFIG | uA | FLOAT
10246 | 40 | 6 | SMOKE SENSOR - MIN I Txon THRESHOLD CONFIG | uA | FLOAT
10247 | 40 | 7 | SMOKE SENSOR - MAX I Rxon THRESHOLD CONFIG | uA | FLOAT
10248 | 40 | 8 | SMOKE SENSOR - MIN I Rxon THRESHOLD CONFIG | uA | FLOAT
10249 | 40 | 9 | SMOKE SENSOR - MAX I Rxoff THRESHOLD CONFIG | uA | FLOAT
10250 | 40 | 10 | SMOKE SENSOR - MIN I Rxoff THRESHOLD CONFIG | uA | FLOAT
10251 | 40 | 11 | SMOKE SENSOR - AVG BUFFER SAMPLES | --- | UI32
10252 | 40 | 12 | SMOKE SENSOR - MAX ERROR COUNTER | --- | UI32
10496 | 41 | 0 | STAND ALONE - CONFIGURATION REGISTER | --- | FLAGS
10497 | 41 | 1 | STAND ALONE - CONFIGURATION MODE | --- | UI32
10498 | 41 | 2 | STAND ALONE - INPUT MODE | --- | UI32
10499 | 41 | 3 | STAND ALONE - RELAY INTERFACE COMPATIBILITY REGISTER | --- | FLAGS
10500 | 41 | 4 | STAND ALONE - MAX GRID VOLTAGE (for LOM OK) | Vac | FLOAT
10501 | 41 | 5 | STAND ALONE - MIN GRID VOLTAGE (for LOM NOT OK) | Vac | FLOAT
10502 | 41 | 6 | STAND ALONE - TIMEOUT GRID VOLTAGE (for LOM OK) | ms | UI32
10503 | 41 | 7 | STAND ALONE - TIMEOUT GRID VOLTAGE (for LOM NOT OK) | ms | UI32
10504 | 41 | 8 | STAND ALONE - DELAY BEFORE NEXT CONNECTION | ms | UI32
10505 | 41 | 9 | STAND ALONE - MIN BATTERY SOC FIRST CONNECTION | % | FLOAT
10506 | 41 | 10 | STAND ALONE - MIN BATTERY SOC NEXT CONNECTION | % | FLOAT
10507 | 41 | 11 | STAND ALONE - MIN BATTERY SOC DISCONNECTION | % | FLOAT
10508 | 41 | 12 | STAND ALONE - NOMINAL VOLTAGE | V | FLOAT
10509 | 41 | 13 | STAND ALONE - FREQUENCY | Hz | FLOAT
10510 | 41 | 14 | STAND ALONE - PEAK CURRENT SATURATION | A | FLOAT
10511 | 41 | 15 | STAND ALONE - OUTPUT OVER VOLTAGE RMS THRESHOLD | V | FLOAT
10512 | 41 | 16 | STAND ALONE - OUTPUT OVER VOLTAGE TIMEOUT | ms | UI32
10513 | 41 | 17 | STAND ALONE - OUTPUT UNDER VOLTAGE RMS THRESHOLD | V | FLOAT
10514 | 41 | 18 | STAND ALONE - OUTPUT UNDER VOLTAGE TIMEOUT | ms | UI32
10515 | 41 | 19 | STAND ALONE - OUTPUT PEAK OVER VOLTAGE THRESHOLD | V | FLOAT
10516 | 41 | 20 | STAND ALONE - OUTPUT PEAK OVER VOLTAGE TIMEOUT | ms | UI32
10517 | 41 | 21 | STAND ALONE - OUTPUT OVER CURRENT RMS THRESHOLD | A | FLOAT
10518 | 41 | 22 | STAND ALONE - OUTPUT OVER CURRENT TIMEOUT | ms | UI32
10519 | 41 | 23 | STAND ALONE - OUTPUT OVER LOAD POWER THRESHOLD | W | FLOAT
10520 | 41 | 24 | STAND ALONE - OUTPUT OVER LOAD POWER TIMEOUT | ms | UI32
10521 | 41 | 25 | STAND ALONE - OUTPUT OVER LOAD VOLT THRESHOLD | V | FLOAT
10522 | 41 | 26 | STAND ALONE - OUTPUT OVER LOAD VOLT TIMEOUT | ms | UI32
10523 | 41 | 27 | STAND ALONE - Pmax (par. 521) RESPECT TO Pnom (par. 530) GAIN | --- | FLOAT
10524 | 41 | 28 | STAND ALONE - Pmax (par. 521) RESPECT TO Pnom (par. 530) OFFSET | W | FLOAT
10525 | 41 | 29 | STAND ALONE - Pmax Absolute | W | FLOAT
10752 | 42 | 0 | AUX. BULK FEED - CONFIGURATION REGISTER | --- | FLAGS
10753 | 42 | 1 | AUX. BULK FEED - MAX VIN FOR CONNECTION | V | FLOAT
10754 | 42 | 2 | AUX. BULK FEED - MIN VBULK FOR CONNECTION | V | FLOAT
10755 | 42 | 3 | AUX. BULK FEED - CHECK FOR CONNECTION TOUT | ms | UI32
11008 | 43 | 0 | HIGH FREQUENCY INJECTION CONFIGURATION REGISTER | --- | FLAGS
11009 | 43 | 1 | FREQUENCY INJECTION | Hz | FLOAT
11010 | 43 | 2 | FREQUENCY BAND AMPLITUDE INJECTION | Hz | FLOAT
65280 | 255 | 0 | DEBUG CONFIGURATION REGISTER 0 (supervisor) | --- | FLAGS
65281 | 255 | 1 | DEBUG CONFIGURATION REGISTER 1 (supervisor) | --- | FLAGS
65282 | 255 | 2 | DEBUG CONFIGURATION REGISTER 2 (supervisor) | --- | FLAGS
65283 | 255 | 3 | DEBUG CONFIGURATION REGISTER 3 (supervisor) | --- | FLAGS
65284 | 255 | 4 | DEBUG CONFIGURATION REGISTER 4 (supervisor) | --- | FLAGS
65285 | 255 | 5 | DEBUG CONFIGURATION REGISTER 5 (supervisor) | --- | FLAGS
65286 | 255 | 6 | DEBUG CONFIGURATION REGISTER 6 (supervisor) | --- | FLAGS
65287 | 255 | 7 | DEBUG CONFIGURATION REGISTER 7 (supervisor) | --- | FLAGS
65288 | 255 | 8 | DEBUG CONFIGURATION REGISTER 8 (supervisor) | --- | FLAGS
65289 | 255 | 9 | DEBUG CONFIGURATION REGISTER 9 (supervisor) | --- | FLAGS
65290 | 255 | 10 | DEBUG FLOAT VALUE 0 (supervisor) | --- | FLOAT
65291 | 255 | 11 | DEBUG FLOAT VALUE 1 (supervisor) | --- | FLOAT
65292 | 255 | 12 | DEBUG FLOAT VALUE 2 (supervisor) | --- | FLOAT
65293 | 255 | 13 | DEBUG FLOAT VALUE 3 (supervisor) | --- | FLOAT
65294 | 255 | 14 | DEBUG FLOAT VALUE 4 (supervisor) | --- | FLOAT
65295 | 255 | 15 | DEBUG FLOAT VALUE 5 (supervisor) | --- | FLOAT
65296 | 255 | 16 | DEBUG FLOAT VALUE 6 (supervisor) | --- | FLOAT
65297 | 255 | 17 | DEBUG FLOAT VALUE 7 (supervisor) | --- | FLOAT
65298 | 255 | 18 | DEBUG FLOAT VALUE 8 (supervisor) | --- | FLOAT
65299 | 255 | 19 | DEBUG FLOAT VALUE 9 (supervisor) | --- | FLOAT
65300 | 255 | 20 | DEBUG UI32 VALUE 0 (supervisor) | --- | UI32
65301 | 255 | 21 | DEBUG UI32 VALUE 1 (supervisor) | --- | UI32
65302 | 255 | 22 | DEBUG UI32 VALUE 2 (supervisor) | --- | UI32
65303 | 255 | 23 | DEBUG UI32 VALUE 3 (supervisor) | --- | UI32
65304 | 255 | 24 | DEBUG UI32 VALUE 4 (supervisor) | --- | UI32
65305 | 255 | 25 | DEBUG UI32 VALUE 5 (supervisor) | --- | UI32
65306 | 255 | 26 | DEBUG UI32 VALUE 6 (supervisor) | --- | UI32
65307 | 255 | 27 | DEBUG UI32 VALUE 7 (supervisor) | --- | UI32
65308 | 255 | 28 | DEBUG UI32 VALUE 8 (supervisor) | --- | UI32
65309 | 255 | 29 | DEBUG UI32 VALUE 9 (supervisor) | --- | UI32
Note on D2: Emanuele Pancani: Bit 0: POWER SAVING EN Bit 1: DC STRING SELF CHECK Bit 2-31: Reserved
Note on D30: botarelli: Bit 0 : Enable (first scan after connection) Bit 1 : Enable (periodic scan) Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D35: Emanuele Pancani: Bit N: 0 = STEP, 1 = LINEAR Central Inv: Bit 3: CQC UV prevails
Note on D36: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D37: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D38: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D39: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D40: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D41: Emanuele Pancani: Bit 0: OV Bit 1: OV2 Bit 2: OV3 Bit 3: OV4 Bit 4: OV5 Bit 5: OV6 Bit 6: OV7 Bit 7: OV8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: OV_AVG_10_MIN Bit 15: OV_PEAK Bit 16: UV Bit 17: UV2 Bit 18: UV3 Bit 19: UV4 Bit 20: UV5 Bit 21: UV6 Bit 22: UV7 Bit 23: UV8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D42: Emanuele Pancani: Bit0: SPLIT PHASE
Note on D47: Var Ph-N
Note on D121: Belli Marco: qualsiasi numero va bene
Note on D122: Belli Marco: va inserito un numero minore di 512
Note on D123: Belli Marco: bit 0: regulator enable/disable (1/0) bit 1: release power with slow speed enable/disable (1/0)
Note on D134: Emanuele Pancani: Bit N: 0 = STEP, 1 = LINEAR
Note on D135: Emanuele Pancani: Bit 0: OF Bit 1: OF2 Bit 2: OF3 Bit 3: OF4 Bit 4: OF5 Bit 5: OF6 Bit 6: OF7 Bit 7: OF8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: rsvd Bit 15: rsvd Bit 16: UF Bit 17: UF2 Bit 18: UF3 Bit 19: UF4 Bit 20: UF5 Bit 21: UF6 Bit 22: UF7 Bit 23: UF8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D136: Emanuele Pancani: Bit 0: OF Bit 1: OF2 Bit 2: OF3 Bit 3: OF4 Bit 4: OF5 Bit 5: OF6 Bit 6: OF7 Bit 7: OF8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: rsvd Bit 15: rsvd Bit 16: UF Bit 17: UF2 Bit 18: UF3 Bit 19: UF4 Bit 20: UF5 Bit 21: UF6 Bit 22: UF7 Bit 23: UF8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D137: Emanuele Pancani: Bit 0: OF Bit 1: OF2 Bit 2: OF3 Bit 3: OF4 Bit 4: OF5 Bit 5: OF6 Bit 6: OF7 Bit 7: OF8 Bit 8: rsvd Bit 9: rsvd Bit 10: rsvd Bit 11: rsvd Bit 12: rsvd Bit 13: rsvd Bit 14: rsvd Bit 15: rsvd Bit 16: UF Bit 17: UF2 Bit 18: UF3 Bit 19: UF4 Bit 20: UF5 Bit 21: UF6 Bit 22: UF7 Bit 23: UF8 Bit 24: rsvd Bit 25: rsvd Bit 26: rsvd Bit 27: rsvd Bit 28: rsvd Bit 29: rsvd Bit 30: rsvd Bit 31: rsvd
Note on D175: Belli Marco: bit 0 : disable/enable (1/0) threshold 1 bit 1 : disable/enable (1/0) threshold 2 bit 31 : disable/enable (1/0) dc injection current regulator
Note on D184: Belli Marco: bit 0 : enable/disable (1/0) bit 1 : ovf Enable bit 2 : uvf Enable bit 3 : standing power (en/dis) bit 4 : release ramp en (en/dis) bit 8-11 : ramp release type (ARN=0, CEI-021=1, CEI-016=2)
Note on D200: STRING: Bit 0 : A.I. pulse mode enable Bit 1 : 0 reduce power 1 gate stop Bit 2 : 1 go to error state Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : 0 reduce grid interface thr times 1 don't reduce grid interface thr Bit 8-11 : pulse duration Bit 12-15 : consecutive detect threshold Bit 16-31 : Reserved CORE: Bit 0 : A.I. pulse mode enable Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8-11 : pulse duration Bit 12-15 : consecutive detect threshold Bit 16-31 : Reserved
Note on D210: Belli: Bit 0 : passive anti islanding mode enable Bit 1 : 0 reduce power 1 gate stop Bit 2 : 1 go to error state Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : 0 reduce grid interface thr times 1 don't reduce grid interface thr Bit 8-11 : pulse duration Bit 12-15 : consecutive detect threshold Bit 16-31 : Reserved
Note on D215: Belli: Bit 0 : 1 active shift enable 0 active shift disable Bit 1-31 :Reserved
Note on D217: (old var 4, low part) • Bit 0 : AFD EN / _DIS • Bit 1 : Perturbation EN / _DIS
Note on D218: ( Old var. 4 , High Byte,Default = 550 msec) • Minimum amount of time necessary to have Tdrift before actuating the Island detection ( to prevent from false positive Islands)
Note on D219: (Old var. 71, High Byte, default = 0.030 Hz) • Is the lower delta frequency threshold, it means the system must now start using the variable Delta F, with Kp variable (1st level), instead of the “simple” fixed one
Note on D220: (Old var. 69, High Byte, default = 0.100 Hz) • Is the higher delta frequency threshold, it means the system must now start using the variable Delta F, with Kp 2nd level, instead of Kp 1st level. This condition in logical “AND” with the first level threshold overrided for n (var. 1604) consecutive times
Note on D221: (Old var. 69, bits 4-7, default = 4) • See var. 1603 description
Note on D222: (Old var. 70, HIGH BYTE, default = 0.090 Hz)
Note on D223: (Old var. 69, bits 0-3, default = 2)
Note on D224: (Old var. 70, LOW BYTE, default =5)
Note on D225: (Old HARD CODED, default = 5)
Note on D226: (Old HARD CODED, default =5)
Note on D227: (Old var. 71, low byte, default =0.700 Hz) • To be summed/subtracted by the first level Overfrequency/underfrequency thresholds to have the ISLAND DETECTED condition TRUE
Note on D228: Pancani: Bit 0 : Bypass EN Bit 1 : Third Harmonic Inj EN Bit 2 : Pre-charge EN Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D229: botarelli: Bit 0 : OV Bit 1 : OV (mid-bulk) Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : OV Absolute Bit 8 : UV Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : OUT OF RANGE (mid-bulk) Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D261: Emanuele Pancani: Bit0-7: MPPT Channel 1-8 ON/OFF Bit8-15: MPPT Type Bit16 : rsvd Bit17-31: rsvd
Note on D275: Belli Marco: bit0: general enable bit1: always bit2: after grid fault bit16-19: mode 0= %Pnom/min 1= %Imax/min
Note on D280: Belli Marco: bit0: general enable
Note on D287: botarelli: Bit 0 : Test enable Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D289: Botarelli Andrea: Expressed as ΔV/Vnom per second
Note on D290: Botarelli Andrea: Expressed as Hz per second
Note on D291: bit0 = 1 -> DSP menage LVRT
Note on D292: bit0 = 1 -> DSP menage LVRT bit8 = 1 -> disable freeze Iq current prefault in symmetric fault ride through bit9 = 1 -> disable freeze Iq current prefault in asymmetric fault ride through
Note on D315: Bit 0 : Gate block Low voltage enable Bit 1 : Gate block High voltage enable Bit 2 : Gate block DeltaV enable Bit 3 : Gate block Current error enable Bit 4 : Gate block dv/dt enable Bit 5 : Gate block neg peak high enable Bit 16 : FFWD not filtred enable for LV Bit 17 : FFWD not filtred enable for HV Bit 18 : FFWD not filtred enable for DELTAV Bit 19 : FFWD not filtred enable for Current Error Bit 20 : FFWD not filtred enable for dV/dt Bit 21 : FFWD not filtred enable for Negative Peak High Bit 22 : FFWD not filtred enable for LVRT exit
Note on D325: Bit 0 : Global Enable 0=disable Bit 1 : Voltage Enable Bit 2 : Frequency Enable Bit 3 : Mode 0=PowerReduction 1=GateOFF Bit 4 : reduce reactive enable, 0=don't reduce reactive; 1= reduce reactive too
Note on D335: botarelli: Bit 0 : R-ISO check enable (TL un-grounded models) Bit 1 : R-ISO self-test enable (TL un-grounded models) Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Grounded pole isolation check (TL grounded models or ISO models) Bit 17 : Grounding mode validity check (TL grounded models or ISO models) Bit 18 : Ground voltage 1 protection enable (TL grounded models or ISO models) Bit 19 : Ground voltage 2 protection enable (TL grounded models or ISO models) Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D336: botarelli: 0 = No grounding 1 = Grounding kit (TL amorphous mode) 2 = G.F.I. UL mode (fuse current check) 3 = G.F.I. European mode (PTC check)
Note on D347: botarelli: Bit 0 : General disable (1 leakage disabled) Bit 1 : sensor degauss disable (1- degauss disable) Bit 2 : sensor self test disable (1- self test disable) Bit 3 : rms abs thr disable (1-disable 0-enable) Bit 4 : rms dyn thr low disable (1-disable 0-enable) Bit 5 : rms dyn thr mid disable (1-disable 0-enable) Bit 6 : rms dyn thr high disable (1-disable 0-enable) Bit 7 : resistive rms abs thr disable (1-disable 0-enable) Bit 8 : resistive rms dyn thr low disable (1-disable 0-enable) Bit 9 : resistive rms dyn thr mid disable (1-disable 0-enable) Bit 10 : resistive rms dyn thr high disable (1-disable 0-enable) Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D364: botarelli: Bit 0 : Contry selection timeout enable Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Contry selection freeze enable Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D365: botarelli: As the "old" var. 8
Note on D366: botarelli: As the "old" var. 215
Note on D367: botarelli: As the "old" var. 211
Note on D387: Meacci: Bit 0 : OPEN_LOOP_EN Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D391: User to define pac max for frequency derating
Note on D408: botarelli: Bit 0 : Derating control 0 Bit 1 : Derating control 1 Bit 2 : Derating control 2 Bit 3 : Derating control 3 Bit 4 : Derating control 4 Bit 5 : Derating control 5 Bit 6 : Derating control 6 Bit 7 : Derating control 7 Bit 8 : Derating control 8 Bit 9 : Derating control 9 Bit 10 : Derating control 10 Bit 11 : Derating control 11 Bit 12 : Derating control 12 Bit 13 : Derating control 13 Bit 14 : Derating control 14 Bit 15 : Derating control 15 Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D409: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D410: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E411: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E412: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D414: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D416: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D417: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E418: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E419: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D421: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D423: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D424: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E425: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E426: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D428: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D430: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D431: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E432: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E433: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D435: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D437: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D438: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E439: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E440: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D442: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D444: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D445: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E446: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E447: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D449: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D451: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D452: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E453: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E454: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D456: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D458: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D459: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E460: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E461: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D463: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D465: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D466: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E467: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E468: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D470: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D472: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D473: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E474: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E475: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D477: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D479: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D480: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E481: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E482: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D484: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D486: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D487: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E488: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E489: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D491: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D493: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D494: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E495: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E496: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D498: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D500: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D501: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E502: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E503: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D505: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D507: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D508: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E509: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E510: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D512: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D514: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D515: botarelli: Bit 0-15 : Parameter index (as defined by the POWERCOM std - see CMD 2-3) Bit 16-23 : Parameter data-type (as defined by the POWERCOM std - see CMD 2-3) Bit 24-31 : Parameter target device ID (as defined by the POWERCOM std) NOTE: The target device ID = 0xFF will be used for forcing the parameter run-time update (using CMD 3) on ALL the POWERCOM nodes
Note on E516: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E517: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D519: Register bits meaning: Bit 1 : Enable ramp regulation when control parameter has to be increased Bit 2 : Enable ramp regulation when control parameter has to be decreased Bit 3 : Enable return with histeresis Bit 4 : Enable output saturation on value imposed by Ostart when I < Istart Bit 8-15 : Position of the flag that signals the derating effective application on the PCOM derating register bit-mask (0-31) Bit 16-23 : Position of the flag that signals the derating effective application on the external protocol derating register bit-mask (0-31) (Ex. The derating register used in the CMD 153 of the Aurora RS485 protocol) Bit 24-31 : Percentile value of the input measure STOP value used as return's value from the histeresis
Note on D521: Meacci: Bit 0 : OTH protection 0 Bit 1 : OTH protection 1 Bit 2 : OTH protection 2 Bit 3 : OTH protection 3 Bit 4 : OTH protection 4 Bit 5 : OTH protection 5 Bit 6 : OTH protection 6 Bit 7 : OTH protection 7 Bit 8 : OTH protection 8 Bit 9 : OTH protection 9 Bit 10 : OTH protection 10 Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : UTH protection 0 Bit 17 : UTH protection 1 Bit 18 : UTH protection 2 Bit 19 : UTH protection 3 Bit 20 : UTH protection 4 Bit 21 : UTH protection 5 Bit 22 : UTH protection 6 Bit 23 : UTH protection 7 Bit 24 : UTH protection 8 Bit 25 : UTH protection 9 Bit 26 : UTH protection 10 Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D522: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D527: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D532: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D537: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D542: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D547: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D552: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D557: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D562: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D567: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D572: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D577: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D582: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D587: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D592: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D597: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D602: Meacci: Bit 0 : Fan control 0 Bit 1 : Fan control 1 Bit 2 : Fan control 2 Bit 3 : Fan control 3 Bit 4 : Fan control 4 Bit 5 : Fan control 5 Bit 6 : Fan control 6 Bit 7 : Fan control 7 Bit 8 : Fan control 8 Bit 9 : Fan control 9 Bit 10 : Fan control 10 Bit 11 : Fan control 11 Bit 12 : Fan control 12 Bit 13 : Fan control 13 Bit 14 : Fan control 14 Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D603: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D604: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D605: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E606: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E607: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D610: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D611: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D612: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E613: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E614: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D617: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D618: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D619: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E619: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E620: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D624: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D625: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on E625: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D626: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E626: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D631: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E631: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D632: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on E632: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D633: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D638: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E638: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D639: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D640: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E643: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D645: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D646: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D647: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E649: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E650: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D652: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D653: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D654: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E655: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E656: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D659: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D660: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D661: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E661: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E662: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D666: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D667: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on E667: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D668: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E668: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D673: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E673: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D674: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on E674: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D675: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D680: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E680: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D681: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D682: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E685: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D687: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on D688: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D689: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E691: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E692: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D694: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E694: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D695: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D696: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E698: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E699: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D701: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E701: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D702: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D703: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E705: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E706: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D708: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan control PCOM cmd index (see CMD 4) Owner is supervisor : The index of the HW fan control channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E708: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D709: botarelli: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) NOTE: The most significant bit (7th) of the data-type field defines the derating-start policy based on the input measure value: MSb = 0 : Derating starts if Meas > Meas_START MSb = 1 : Derating starts if Meas > Meas_STOP Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D710: botarelli: Bit 24-31 : Fan owner device ID (as defined by the POWERCOM std - if the value is 255 then the ctrl owner is the supervisor itself) Bit 0-15 : Owner is an ext. PCOM device : Fan speed measure index (see CMD 1) Owner is supervisor : The index of the HW fan speed read channel (see IO_profile... source code) Bit 16-23 : Owner is an ext. PCOM device : Fan control PCOM cmd data-type (see CMD 4) Owner is supervisor : Always UInt32 (4)
Note on E712: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on E713: botarelli: The unit for the input measure refers to the selected measure ID (see CMD 1)
Note on D717: Baud-rate codes: 0:2400 1:4800 2:9600 3:19200 4:34800 5:57600 6:115200
Note on D718: Protocol codes: 0:Aurora (slave) 1:Modbus RTU (slave)
Note on D719: Parity codes: 0 = No parity 1 = Even parity 2 = Odd parity
Note on D721: Baud-rate codes: 0:2400 1:4800 2:9600 3:19200 4:34800 5:57600 6:115200
Note on D722: Protocol codes: 0:Aurora (slave) 1:Modbus RTU (slave)
Note on D723: Parity codes: 0 = No parity 1 = Even parity 2 = Odd parity
Note on D724: Turchini Francesco: Bit 0 : DIN 0 Bit 1 : DIN 1 Bit 2 : DIN 2 Bit 3 : DIN 3 Bit 4 : DIN 4 Bit 5 : DIN 5 Bit 6 : DIN 6 Bit 7 : DIN 7 Bit 8 : DIN 8 Bit 9 : DIN 9 Bit 10 : DIN 10 Bit 11 : DIN 11 Bit 12 : DIN 12 Bit 13 : DIN 13 Bit 14 : DIN 14 Bit 15 : DIN 15 Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D725: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D727: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D728: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D730: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D731: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D733: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D734: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D736: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D737: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D739: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D740: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D742: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D743: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D745: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D746: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D748: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D749: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D751: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D752: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D754: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D755: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D757: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D758: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D760: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D761: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D763: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D764: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D766: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D767: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D769: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D770: Turchini Francesco: 0 = Remote-Off 1 = StandAlone 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D772: Turchini Francesco: Bit 0 : Polarity Input Bit 1 : Low to High Transition Bit 2 : High to Low Transition Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D773: Turchini Francesco: Bit 0 : DIN 0 Bit 1 : DIN 1 Bit 2 : DIN 2 Bit 3 : DIN 3 Bit 4 : DIN 4 Bit 5 : DIN 5 Bit 6 : DIN 6 Bit 7 : DIN 7 Bit 8 : DIN 8 Bit 9 : DIN 9 Bit 10 : DIN 10 Bit 11 : DIN 11 Bit 12 : DIN 12 Bit 13 : DIN 13 Bit 14 : DIN 14 Bit 15 : DIN 15 Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D774: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D777: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D780: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D783: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D786: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D789: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D792: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D795: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D798: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D801: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D804: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D807: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D810: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D813: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D816: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D819: Turchini Francesco: 0 = Alarm-Contact (production) 1 = Alarm-Contact (alarm ALL - no-latch) 2 = Alarm-Contact (alarm configurable - no-latch) 3 = Alarm-Contact (crepuscolar) 4 = Alarm-Contact (alarm ALL - latch) 5 = Alarm-Contact (alarm configurable - latch) 6 = Alarm-Contact (alarm configurable - matrix) 65536 = Custom function 0 65537 = Custom function 1 ...
Note on D822: botarelli: Bit 0 : Reserved Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D823: botarelli: 0=No regulation 1=Apply user P/Pmax set-point
Note on D826: botarelli: 0=Slope mode 1=Trip-time mode
Note on D827: botarelli: Bit 0 : COS-PHI sign inverted Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D828: botarelli: 0=No regulation 2-3=Q set-point 4=Cos-Phi set-point 9=Cos-Phi=f(P) 10=Q=f(U) 11=Slovenian
Note on D831: botarelli: 0=Slope mode 1=Trip-time mode
Note on D832: botarelli: A value of 0 disables the threshold
Note on D833: botarelli: A value of 0 disables the threshold
Note on D834: botarelli: A value of 0 disables the threshold
Note on D835: botarelli: A value of 0 disables the threshold
Note on D967: botarelli: Bit 0 : Mask communication error (E005) when ALL PCOM nodes are found off-line Bit 1 : Enter low-power mode in stand-by state Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D968: botarelli: - If communication error (E005) is not masked then this time represents the timeout for the error when ALL PCOM nodes are found off-line - If communication error (E005) is masked then this time represents the timeout for entering the low-power mode in stand-by state
Note on D969: botarelli: Bit 0 : AFD management enable Bit 1 : AFD check enable Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D970: Turchini Francesco: number of up-count ticks threshold [100 us] before signal an arc fault
Note on D971: Turchini Francesco: number of down-count ticks threshold [100 us] before signal a generic fault
Note on D972: Turchini Francesco: number of down-count ticks threshold [100 us] before signal a generic fault
Note on D973: botarelli: Bit 0-7 : First day of the week - 0 : Sunday - 1 : Monday - 3-255 : Not valid Bit 8-31 : Reserved
Note on D1601: botarelli: 0 : English 1 : Italian 2 : German 3 : Spanish 4 : French 5 : Czech 6 : Dutch
Note on D1603: botarelli: Range [0 - 9]
Note on D1604: botarelli: Range [0 - 9]
Note on D1605: botarelli: 0 : Always off 1 : Always on 2 : Auto off
Note on D1608: botarelli: Bit 0 : Stay in recovery after any alarm Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1609: Turchini Francesco: Time to hold close a Relay before read the voltage measure between relays poles
Note on D1610: Turchini Francesco: Minimum voltage value necessary to consider test relay OK
Note on D1611: Turchini Francesco: Delay time to wait for with RISO relay close (to permit charger of various board capacity) before to make a new read of Voltage on relay poles
Note on D1612: Turchini Francesco: Minimum voltage variation to consider test relay OK with relay RISO closed
Note on D1613: Turchini Francesco: Bit 0 : Allowed Relay Board ID = 0 Bit 1 : Allowed Relay Board ID = 1 Bit 2 : Allowed Relay Board ID = 2 Bit 3 : Allowed Relay Board ID = 3 Bit 4 : Allowed Relay Board ID = 4 Bit 5 : Allowed Relay Board ID = 5 Bit 6 : Allowed Relay Board ID = 6 Bit 7 : Allowed Relay Board ID = 7 Bit 8 : Allowed Relay Board ID = 8 Bit 9 : Allowed Relay Board ID = 9 Bit 10 : Allowed Relay Board ID = 10 Bit 11 : Allowed Relay Board ID = 11 Bit 12 : Allowed Relay Board ID = 12 Bit 13 : Allowed Relay Board ID = 13 Bit 14 : Allowed Relay Board ID = 14 Bit 15 : Allowed Relay Board ID = 15 Bit 16 : Allowed Relay Board ID = 16 Bit 17 : Allowed Relay Board ID = 17 Bit 18 : Allowed Relay Board ID = 18 Bit 19 : Allowed Relay Board ID = 19 Bit 20 : Allowed Relay Board ID = 20 Bit 21 : Allowed Relay Board ID = 21 Bit 22 : Allowed Relay Board ID = 22 Bit 23 : Allowed Relay Board ID = 23 Bit 24 : Allowed Relay Board ID = 24 Bit 25 : Allowed Relay Board ID = 25 Bit 26 : Allowed Relay Board ID = 26 Bit 27 : Allowed Relay Board ID = 27 Bit 28 : Allowed Relay Board ID = 28 Bit 29 : Allowed Relay Board ID = 29 Bit 30 : Allowed Relay Board ID = 30 Bit 31 : Allowed Relay Board ID = 31
Note on D1614: Central Inv.: bit 0 : Bulk voltage loop enable
Note on D1639: botarelli: Bit 0 : System stop after bundle check fault enable Bit 1 : FW backup on targets enable Bit 2 : Update on equal versions enable Bit 3 : Skip update version check enable Bit 4-7 : Reserved Bit 8-15 : GS reload policy for internal updates Bit 16-31 : Reserved
Note on D1640: Meacci: Bit 0 : PWM control 0 Bit 1 : PWM control 1 Bit 2 : PWM control 2 Bit 3 : PWM control 3 Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1641: Meacci Lorenzo: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1)(it has to be equal to 0xFF) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D1642: Meacci Lorenzo: Bit 0-15 : the index of the used HW PWM control timer Bit 16-23 : always UInt32 (4) Bit 24-31 : PWM timer owner device ID (as defined by the POWERCOM std - if the value is 255 then the owner is the supervisor itself)(it has to be equal to 0xFF)
Note on D1644: Meacci Lorenzo: Bit 0-2 : PWM timer prescaler value Bit 3-4 : PWM timer clock edge select value Bit 5-7 : PWM timer counter clear value Bit 8-11 : PWM timer capture edge value Bit 12-15 : PWM timer capture edge duty value Bit 16-31 : Reserved
Note on D1645: Meacci Lorenzo: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1)(it has to be equal to 0xFF) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D1646: Meacci Lorenzo: Bit 0-15 : the index of the used HW PWM control timer Bit 16-23 : always UInt32 (4) Bit 24-31 : PWM timer owner device ID (as defined by the POWERCOM std - if the value is 255 then the owner is the supervisor itself)(it has to be equal to 0xFF)
Note on D1648: Meacci Lorenzo: Bit 0-2 : PWM timer prescaler value Bit 3-4 : PWM timer clock edge select value Bit 5-7 : PWM timer counter clear value Bit 8-11 : PWM timer capture edge value Bit 12-15 : PWM timer capture edge duty value Bit 16-31 : Reserved
Note on D1649: Meacci Lorenzo: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1)(it has to be equal to 0xFF) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D1650: Meacci Lorenzo: Bit 0-15 : the index of the used HW PWM control timer Bit 16-23 : always UInt32 (4) Bit 24-31 : PWM timer owner device ID (as defined by the POWERCOM std - if the value is 255 then the owner is the supervisor itself)(it has to be equal to 0xFF)
Note on D1652: Meacci Lorenzo: Bit 0-2 : PWM timer prescaler value Bit 3-4 : PWM timer clock edge select value Bit 5-7 : PWM timer counter clear value Bit 8-11 : PWM timer capture edge value Bit 12-15 : PWM timer capture edge duty value Bit 16-31 : Reserved
Note on D1653: Meacci Lorenzo: Bit 0-15 : Measure index (as defined by the POWERCOM std - see CMD 1) Bit 16-23 : Measure data-type (as defined by the POWERCOM std - see CMD 1) Bit 24-31 : Measure owner device ID (as defined by the POWERCOM std - see CMD 1)(it has to be equal to 0xFF) NOTE: The owner device ID = 0xFF will be used for referencing the internal measures list of the device that manages the system parameters (Ex. The Aurora CMD 59 measures system Supervisor)
Note on D1654: Meacci Lorenzo: Bit 0-15 : the index of the used HW PWM control timer Bit 16-23 : always UInt32 (4) Bit 24-31 : PWM timer owner device ID (as defined by the POWERCOM std - if the value is 255 then the owner is the supervisor itself)(it has to be equal to 0xFF)
Note on D1656: Meacci Lorenzo: Bit 0-2 : PWM timer prescaler value Bit 3-4 : PWM timer clock edge select value Bit 5-7 : PWM timer counter clear value Bit 8-11 : PWM timer capture edge value Bit 12-15 : PWM timer capture edge duty value Bit 16-31 : Reserved
Note on D1673: Meacci Lorenzo: Bit 0 : INTERCOM_BYPASS_EN Bit 1 : INIT_BLOCK_BYPASS_EN Bit 2 : POWER_MASTER_MODE_EN Bit 3 : AI_MASTER_MODE_EN Bit 4 : PWM_MASTER_MODE_EN Bit 5 : FAN_SUPPLY_MANAGEMENT_EN Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1674: Meacci Lorenzo: Time used to force in night mode the passage in the supervisor init state
Note on D1675: Meacci Lorenzo: Time used to reset (at the morning) the alarm occurence counters
Note on D1676: Meacci Lorenzo: Time used to keep lit the fans after a fault occurrence
Note on D1677: Meacci Lorenzo: Awaited time before reporting a "Fan Stuck" fault
Note on D1678: Meacci Lorenzo: Time used to keep active the night mode before the commutation of the energy save output
Note on D1681: Bit 6 : SYS_CONTROLLER_COMM_ERR_MASK_EN
Note on D1682: Francesco Turchini: Bit 0 : Reserved Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1687: botarelli: Bit 0 : Check general enebale Bit 1 : Sequence sign check enable Bit 2 : Target sequence sign (0 = Negative, 1 = Positive) Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1688: Francesco Turchini: Bit 0 : Enable Smoke Sensor Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1701: Francesco Turchini: Bit 0 : Stand Alone Enable ( 1 = Enabled) Bit 1 : Reset user consent on system restart ( 1 = Enabled) Bit 2 : Reset user consent on disconnection due LOM bit = 0 ( 1 = Enabled) Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1702: Francesco Turchini: Mode 0 : None (stand-alone disabled) Mode 1 : Manual 1 (LOM check required) Mode 2 : Manual 2 (LOM check not required) Mode 2 : Auto
Note on D1703: Turchini Francesco: The stand-alone input will be associated to one of the available DIN (digital-input) configuration slots and the input management mode will be one of the following: Mode 2 : Stand-alone user consent Mode 3 : Stand-alone external alarm
Note on D1704: Turchini Francesco: This register maps the relays interface boards that can be used on the converter for the selected GRID standard. One register will be provided for each available converter family. The register value will be associated to GRID standard (using the Global-Settings management). The register will be formatted as a bit-mask with the following meaning: - Bit 0 : Relays interface board with ID 0 - Bit 1 : Relays interface board with ID 1 ... - Bit 31 : Relays interface board with ID 31 If a bit is 0 then the corresponding relays interface board is NOT allowed for the current family/GRID.
Note on D1731: botarelli: Bit 0 : General enebale Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1735: botarelli: Bit 0 : General enebale Bit 1 : Reserved Bit 2 : Reserved Bit 3 : Reserved Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved
Note on D1738: botarelli: Bit 0 : Stay in recovery after any alarm Bit 1 : Skip AC relays self-test during the grid-tied connection phase Bit 2 : Skip wait for ICOM ready during the system start-up phase Bit 3 : Skip Timeout In Recovery function Bit 4 : Reserved Bit 5 : Reserved Bit 6 : Reserved Bit 7 : Reserved Bit 8 : Reserved Bit 9 : Reserved Bit 10 : Reserved Bit 11 : Reserved Bit 12 : Reserved Bit 13 : Reserved Bit 14 : Reserved Bit 15 : Reserved Bit 16 : Reserved Bit 17 : Reserved Bit 18 : Reserved Bit 19 : Reserved Bit 20 : Reserved Bit 21 : Reserved Bit 22 : Reserved Bit 23 : Reserved Bit 24 : Reserved Bit 25 : Reserved Bit 26 : Reserved Bit 27 : Reserved Bit 28 : Reserved Bit 29 : Reserved Bit 30 : Reserved Bit 31 : Reserved